## Cover
SMU Modbus Protocol Data List (V1.81)
| Prepared By |  | Date
| Reviewed By |  | Date
| Approved By |  | Date
Huawei Technologies Co., Ltd.
All rights reserved.

## Version Information
Version Information
Date | Version | Description | Revision
2017.05.23 | V1.00 | Completed the draft.
2017.06.15 | v1.01 | Add collect information/Configuration Parameters/Alarm Signals for the scc800.
2017.08.01 | v1.02 | Add collect information "Battery SOC in combined cabinet N# N: 1–8; " and "AC Energy Consumption in combined cabinet N# N: 1–8; "
2017.09.05 | v1.03 | Change data type of "Battery Test Average Discharge Current " to INT from UINT
2018.01.31 | v1.04 | Allocate "DG Start Voltage" and "DG Stop Voltage" for ATC project in Configuration-Parameter-Sheet.
2018.01.31 | v1.05 | Allocate address range 0x4024~0x4056 for Spain Cellenx project in Performance-Data-Sheet.
2018.02.03 | v1.06 | Allocate address range 0x501B~0x5022 and 0x5102~0x5103 in Alarm-Singnals-Sheet, address range 0x23F0~0x23F1 in Configuration-Parameters-Sheet for Spain Cellenx project.
2018.05.21 | v1.07 | Allocate address range 0x5023~0x502E in Alarm-Singnals-Sheet for ATC project.
2018.07.05 | V1.08 | Delete: 0x5103 Multiple Rectifier Fault 0x501F LVD Inhibited Modify: 0x5102 All Rectifier Fault ---> Rectifier Abnormal(not standard, for special customer) Add: 0x502F Urgent Alarm (not standard, for special customer) 0x5030 Non-urgent Alarm (not standard, for special customer) 0x5031 Fuse Broken Alarm (not standard, for special customer)
2018.09.11 | V1.09 | Add: First version of SMU11D V500R002C50; Add:0xA710~0xA715 in Collect Information Add:0x2126~0x2128 in Configuration Parameters Add:0x2830~0x285F in Configuration Parameters Add:0x5036~0x5055 in Alarm Signals Add:0x5507~0X5508\0x6001~0x6098in Alarm Signals
2018.11.02 | V1.10 | Add: DPS Add：0x100F~0x1010 in Collect Information Add: 0x2070~0x2073/0x2080~0x2081/0x2090~0x2091 in Configuration Parameters Add：0x5070~0x5075 in Alarm Signals
2018.12.10 | V1.11 | SMU11D Add: 0x1011 in Collect Information 0x2129 in Configuration Parameters
2018.12.20 | V1.12 | SMU11D Add: 0x1012~0x1015 in Collect Information 0x20A0~0x20A3 in Configuration Parameters
2019.01.30 | V1.13 | SMU11D Add:0x1016~0x1021
2019.06.24 | V1.14 | DPS: Add 0x1501 for system input type
2019.10.09 | V1.15 | DPS: Add 0x2130~0x2157 :LLVD5~LLVD7 configuration parameters Add 0x5056~0x505B :LLVD5~LLVD7 alarm signals Add 0x3050~0x3057: LLVD1~LLVD7 ON/OFF Control parameters Add 0x2160~0x2174: LLVD1~LLVD7 Plan Disconnect Parameters
2019.12.13 | V1.16 | DPS: Add 0xA720~0xAF31 :ACB collect signals
2019.12.20 | V1.17 | SMU02C: Add 0x1030~0x1038 :AC2 collect signals Add 0x212B~0x212E：AC2 configuration signals Add 0x405A~0x405E：AC2 performance data Add 0x5076~0x5082：AC2 alarm signals
2019.12.23 | V1.18 | 1.Register 0x2000 , value range 2000~2100 , changed range 2000~2037. 2.Register 0x2301, value range 42~58.3, changed range 42~58. 3.Register 0x2302, value range 42~58.3, changed range 42~58. 4.Register 0x2101, value range 35~56, changed range 36~56. 5.Register 0x2104, value range 35~56, changed range 36~56. 6.Register 0x2304, value range 35~56, changed range 36~56.
2019.12.31 | V1.19 | Add the SMU V500R003C10 list
2020.01.17 | V1.20 | DPS: Add 0x1039~0x103F :DC Load1~7 Voltage Add 0x1040~0x1046 :DC Load1~7 Current Add 0x1047~0x104D :DC Load1~7 Power Add 0x4062~0x407A :Hourly DC Load1~7 Power Consumption Add 0x407E~0x4096 :cumulative DC Load1~7 Power Consumption Modify:0x4004、0x4014，Add Total to the name to distinguish it from the split path, which does not affect compatibility.
2020.01.20 | V1.21 | DPS: Add 0x104E~0x104F :DC Load Number、ESN
2020.02.03 | V1.22 | DPS: Modify 0x104F: ESN，Add remarks "DPS:ESN customized by Rakuten in Japan" Add 0x2175~0x217B：LLVD1~7 Manual Control of Delayed Power-on Time
2020.02.10 | V1.23 | Add SMU V500R003C10(DPS); Modify 0x2050:V500R003C10(DPS) is supported; Delete 0x3050:Definition Duplicate
2020.02.25 | V1.24 | DPS: Add 0x1050~0x1056:DC Load1~7 Contactor Status
2020.03.12 | V1.25 | DPS: Updated the V500R003C10(TR5-2) column as required .
2020.03.14 | V1.26 | DPS: The register of DC Load1~7 Contactor Status conflicts with the register of User Customize ESN,the register of DC Load1~7 Contactor Status was changed to 0x1060~0x1066.
2020.04.15 | V1.27 | DPS: Modify 0x104F: change from "User Customize ESN" to "User Customize QR CODE"
2020.04.21 | V1.28 | DPS: The default value and minimum value of LLVD1~7 Manual Control of Delayed Power-on Time are changed to 0
2020.04.29 | V1.29 | Add: 0x0013 soft entire version
2020.05.08 | V1.30 | Add: SMU11B list
2020.06.08 | V1.31 | Add SMU02C: 1. Register 0x2900 2. Register 0x5036+ (N-1)*1
2020.08.24 | V1.32 | Add DPS: 1. Register 0x2200/0x2201/0x2211/0x2221/0x2231、0x2241~0x2246
2020.09.11 | V1.33 | 1. Changed the lower limit of the AAU output voltage from 55 to 57 and the upper limit from 72.5 to 60. 2. The lower threshold of the AAU Disconnect voltage is changed from 35 to 36.
2020.09.18 | V1.34 | Updated Hourly DC Load1–7 Power Consumption based on the review conclusion of the unified model on the NMS. The DPS does not support signals.
2020.09.28 | V1.35 | The default value and lower limit of AC over/underfrequency are corrected.
2020.11.26 | V1.36 | Add 5G Power V100R021C10(DPS) list
2020.11.28 | V1.37 | Delete DPS V100R002C00 list, this version is SMU V500R003C10; Modify DPS V100R001C50 to SMU V500R003C00;
2020.11.30 | V1.38 | Add 5G Power V100R021C10(SMU02C)list The ETP48400 supports lithium batteries and other related capabilities in the data center FM500 project. The ETP48400 supports the following registers: 0x0013, 0x2251, and ACB lithium battery information (collect and alarm)
2020.11.30 | V1.39 | DPS Add 4.5KW three-live-wire AC,Add: 0x505C~0x5061
2020.12.08 | V1.40 | Add 5G Power V100R021C10(SMU02C): 0x1800、0x1810~0x1814+(N-1)*16、0x4020、0x5900、0x5901~0x5904+(N-1)*16
2020.12.22 | V1.41 | The following registers represent the current and temperature of the lithium battery and are updated to signed values: 0xA704~0xA705、0xA733~0xA734+(N-1)*64、0xA737~0xA738+(N-1)*64、0xA73A~0xA74F+(N-1)*64、0xA76E+(N-1)*64
2020.12.31 | V1.42 | Updated the maximum number of SSU collection and alarm signals to 60, and updated the remaining registers accordingly.
2021.01.19 | V1.43 | Add: 0x5103、0x501F
2021.01.26 | V1.44 | Add solar cabinets list.
2021.04.01 | V1.45 | Address of the Spanish Cellnex Market Allocation Register
2021.04.02 | V1.46 | Modify DPS support list: Battery SOC（0xA739+(N-1)*64）:modify to support Cell Package Current（0xA737~0xA738+(N-1)*64）:modify to not support
2021.04.14 | V1.47 | The address of the register allocated by the Spanish Cellnex market is changed from UINT32 to INT32, and the maximum value collection parameter that is not required for CCB decision-making is deleted.
2021.04.19 | V1.48 | Modify ACB: The unit of Output Power（0xA76B+(N-1)*64）is changed from NA to W; Charge/Discharge Power（0xA715~0xA716）: unit changed to kW, data type changed to INT32, Precision changed to 2; Number of ACB Cabinets（0xA720、0x2900）: description is changed from 10 to 16;
2021.04.22 | V1.49 | 1. Added support for bypass, inverter unit, inverter module, ECM, and iDCDU. 2. Added support for integrated optical storage modules and integrated optical storage module groups.
2021.04.23 | V1.50 | 1. The inverter module alarm is added. 2. Inverter-related signal models, such as fan speed, power factor, and active power, have been deleted. Modbus protocols are also deleted.
2021.04.27 | V1.51 | 1. The accumulated power consumption of the iDCDU and the power consumption of loads 1 to 4 are changed to UINT64. 2. Delete ECM Phase、iDCDU Number in iDCDU Group 3. Added remarks about the differential display of the bypass and ECM in three-phase and single-phase scenarios. 4. Added the inverter load rate, input voltage undervoltage return threshold, and bypass power failure alarms.
2021.05.08 | V1.52 | 1. 0x4024、0x402A、0x4030、0x4036、0x403C、0x4042、0x4048、0x404E、0x4054,the number of bytes is changed from 8 to 4.
2021.05.13 | V1.53 | 1. Add description:0x1560、0x1561、0x1602、0x1603. 2. 0x3032:Multiple lines are incorrectly written and combined into one line.
2021.05.18 | V1.54 | Changed Chinese to English.
2021.05.20 | V1.55 | Add SMU11B V500R003C00.
2021.07.06 | V1.56 | Add columns 5G Power V100R021C91 (SMU02C/02X) and 5G Power V100R021C91 (PC510-IOT) in Public-Information-Sheet、Performance-Data-Sheet.
2021.07.15 | V1.57 | 1. Adjust position of SMU11B V500R003C00 column 2. Add columns: DP-SP V300R022C00(DPS SD5010), DP-SP V300R022C00(SMU02C/02X), DP-SP V300R022C00(DPS A7).
2021.07.26 | V1.58 | Add columns: 5G Power V100R021C10 (SMU11B), DP-SP V300R022C00 (SMU11B). Use SMU11B V500R003C10 column as a template.
2021.08.06 | V1.59 | Add columns: 5G Power V100R021C80 (SMU02C/02X)
2021.08.11 | V1.60 | Delete Single Branch Items: DP-SP V300R022C00(DPS A7).
2021.08.16 | V1.61 | Add Signal Mapping.
2021.08.24 | V1.62 | DP-SP V300R022C00(DPS A7): Modify 0x0001 value from 2 to 49
2021.08.25 | V1.63 | DP-SP V300R022C00(DPS A7): 0xA720 modify from support to no support 0x1101 modify from blank to support
2021.08.26 | V1.64 | 0x2001~0x2005: Add remarks"the threshold is UTC time" 0x2010: Modify threshold according equipment threshold to 1~255
2021.08.26 | V1.65 | DP-SP V300R022C00(DPS A7): 0x20A5~0x20A9 modify from support to no support
2021.08.30 | V1.66 | 0x5101: modify description and mapping signal ID(DTS2021082820701)
2021.09.09 | V1.67 | Add columns: DP-SP V300R022C10
2021.10.13 | V1.68 | 0x2126: modify DPS(A7) from support to no support 0x5036+ (N-1)*1: Refresh the signal mapping relationship
2021.11.11 | V1.69 | Add columns: DP-SP V300R022C10 (Solar Access Controller)
2022.02.16 | V1.70 | Spain Cellnex: 0xD7A0~0xDBAF:Load-iCBD Information 0xDBB0~0xDD9F:Branch Group Information 0xDDA0~0xDDBF:DC Output Distribution Information
2022.03.05 | V1.71 | 0x5036+ (N-1)*1：DP-SP V300R022C00(DPS SD5010)、DP-SP V300R022C10(DPS SD5010) Refresh
2022.03.11 | V1.72 | DP-SP V300R022C10(PVPU) ACB Alarm signal Refresh
2022.04.06 | V1.73 | iSitePower V100R023C92(SMU02C/02X) Load-iCBD/24V Module Group/24V Module/DG signal Refresh
2022.04.25 | V1.74 | DP-SP V300R022C10 (Solar Access Controller)：0x5900、0x3002 modify from support to no support
2022.05.20 | V1.75 | DP-SP V300R022C10 (Solar Access Controller): modify name to DP-SP V300R022C10(PVPU)
2022.06.09 | V1.76 | SMU V500R003C00(DPS)、SMU V500R003C10(DPS)、5G Power V100R021C10(DPS)、DP-SP V300R022C00(DPS SD5010)、DP-SP V300R022C10(DPS SD5010): 0x5100 modify from support to no support
2022.06.14 | V1.77 | Add columns: DP-SP V300R023C00(DPS SD5010)、DP-SP V300R023C00(DPS A7)、DP-SP V300R023C00(SMU02X), Inherited from DP-SP V300R022C10
2022.06.16 | V1.78 | Add iDMU Load-iCBD signal. Change DC Output Distribution Load-iCBD max number to 62, max regitser to 12.
2022.09.01 | V1.79 | Add:(20220829 SEG) 0xA770 +(N-1)*64:Battery Type 0xC670~0xC67E+(N-1)*32:Battery Barcode 0xC67F~0xC681+(N-1)*32:Software Version 0xC682~0xC684+(N-1)*32:Hardware Version 0x217C~0x2184:LLVD1 parameters 0x843E+(N-1)*64:Battery Alarm For ACB
2022.09.15 | V1.80 | Add columns: DP-SP V300R023C10(DPS A7), Inherited from DP-SP V300R023C00
2022.10.25 | V1.81 | Add columns: DP-SP V300R023C10(DPS SD5010), Inherited from DP-SP V300R023C00
2022.11.26 | V1.82 | Add SSU signal: 0x1815~0x1816+(N-1)*16:SSU 1–N Output Power
2022.12.03 | V1.83 | Delete columns: DP-SP V300R023C10(DPS SD5010), no related version exists in DP-SP V300R023C10
2022.01.16 | V1.84 | Add register range: System type(0x0005~0x0012), Software entire version(0x0013~0x0020); Add signal: (for PVPU) Controller type(0x0021), Device ID(0x0022~0x002A), SSU Total Output Power(0x1802~0x1803), PV Adapter 1–N (N=18) Address(0xCA70+(N-1)*32), PV Adapter1–N (N=18) Running State(0xCA71+(N-1)*32), PV Adapter 1–N (N=18) Input Voltage(0xCA72+(N-1)*32), PV Adapter 1–N (N=18) Input Current(0xCA73+(N-1)*32), PV Adapter 1–N (N=18) Output Voltage(0xCA74+(N-1)*32), PV Adapter 1–N (N=18) Output Current(0xCA75+(N-1)*32), PV Adapter 1–N (N=18) Temperature(0xCA76+(N-1)*32), PV Adapter 1–N (N=18) Output Power(0xCA77~0xCA78+(N-1)*32), PV Adapter 1–N (N=18) Software Version(0xCA79~0xCA81+(N-1)*32), PV Adapter 1–N (N=18) Type(0xCA82~0xCA8A+(N-1)*32), DC Overvoltage Threshold(N to Y), SSU Total Output Power Consumption per Day(0x409A), PV Adapter1–N (N=18) Alarm(0xE7D0+(N-1));
2023.05.05 | V1.85 | Add columns: DP-SP V300R024C00(DPS SD5010), Inherited from DP-SP V300R023C00
2023.05.09 | V1.86 | Add columns: DP-SP V300R024C00(SMU02X), Inherited from DP-SP V300R023C00(SMU02X)
2023.11.20 | V1.87 | 1.Add columns: DP-SP V300R024C10(SMU02X), Inherited from DP-SP V300R024C00(SMU02X) 2.Add columns: DP-SP V300R024C10(DPS SD5010), Inherited from DP-SP V300R024C00(DPS SD5010) 3.Add columns: DP-SP V300R024C10(DPS A7), Inherited from DP-SP V300R024C00(DPS A7)

## Public Information
Data | Unit | Register Address | Data Type | Number of Bytes | SMU05A V500R001 C30/C50/C60 | SMU02B V300R002 C10/C20 | SMU02B V300R003 C00/C10 | SMU02B V500R001 C00/C10/C20/C30/C50/C60 | SMU02B V500R002 C00 | SCC800 V100R001C90 | SMU11D V500R002C50 | SMU V500R003C00(DPS) | SMU11B V500R003C00 | SMU V500R003C10(DPS) | SMU02B V500R003C10 | SMU11B V500R003C10 | iSitePower V100R021C10(DPS) | iSitePower V100R021C10 (SMU02C/02X) | iSitePower V100R021C10 (SMU11B) | iSitePower V100R021C10 (Solar cabinet) | iSitePower V100R021C80 (SMU02C/02X) | iSitePower V100R021C91 (PC510-IOT) | iSitePower V100R021C80 (SMU02C/02X) | DP-SP V300R022C00(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C00(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C00(SMU02C/02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C00 (SMU11B) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(SMU02C/02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10 (SMU11B) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(PVPU) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C00(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C00(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C00(SMU02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C10(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C00(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C00(SMU02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C10(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C10(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C10(SMU02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | mark
Manufacturer code | N/A | 0x0000 | UNIT16 | 2 | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | - | 11 | Y | - | 11 | Y | - | 11 | Y | - | 11 | Y | - | 11 | Y | - | 11 | Y | - | 11 | Y | - | 11 | Y | - | 11 | Y | - | 11 | Y | - | 11 | Y | - | 11 | Y | - | 11 | Y | - | 11 | Y | - | 11 | Y | - | 11 | Y | - | 11 | Y | - | 11
Equipment type | N/A | 0x0001 | UNIT16 | 2 | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | - | 48 | Y | - | 49 | Y | - | 2 | Y | - | 3 | Y | - | 48 | Y | - | 49 | Y | - | 2 | Y | - | 3 | Y | - | 48 | Y | - | 48 | Y | - | 49 | Y | - | 2 | Y | - | 49 | Y | - | 48 | Y | - | 2 | Y | - | 49 | Y | - | 48 | Y | - | 2
Protocol version | N/A | 0x0002 | UNIT16 | 2 | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | - | 112 | Y | - | 201 | Y | - | 201 | Y | - | 112 | Y | - | 112 | Y | - | 201 | Y | - | 201 | Y | - | 112 | Y | - | 112 | Y | - | 112 | Y | - | 201 | Y | - | 201 | Y | - | 201 | Y | - | 112 | Y | - | 201 | Y | - | 201 | Y | - | 112 | Y | - | 201
software version | N/A | 0x0003 | UNIT16 | 2 | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | 0x8001 | 0x1174 | Y | 0x2016 | 0x1174 | Y | 0x2016 | 0x1174 | Y | 0x2016 | 0x1174 | Y | 0x8001 | 0x1174 | Y | 0x2016 | 0x1174 | Y | 0x2016 | 0x1174 | Y | 0x2016 | 0x1174 | Y | 0x8001 | 0x1174 | Y | 0x8001 | 0x1174 | Y | 0x2016 | 0x1174 | Y | 0x2016 | 0x1174 | Y | 0x2016 | 0x1174 | Y | 0x8001 | 0x1174 | Y | 0x2016 | 0x1174 | Y | 0x2016 | 0x1174 | Y | 0x8001 | 0x1174 | Y | 0x2016 | 0x1174
hardware version | N/A | 0x0004 | UNIT16 | 2 | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | 0x8001 | 0x1118 | Y | 0x2016 | 0x1118 | Y | 0x2016 | 0x1118 | Y | 0x2016 | 0x1118 | Y | 0x8001 | 0x1118 | Y | 0x2016 | 0x1118 | Y | 0x2016 | 0x1118 | Y | 0x2016 | 0x1118 | Y | 0x8001 | 0x1118 | Y | 0x8001 | 0x1118 | Y | 0x2016 | 0x1118 | Y | 0x2016 | 0x1118 | Y | 0x2016 | 0x1118 | Y | 0x8001 | 0x1118 | Y | 0x2016 | 0x1118 | Y | 0x2016 | 0x1118 | Y | 0x8001 | 0x1118 | Y | 0x2016 | 0x1118
System type | N/A | 0x0005~0x0012 | String | 28 | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | 0x8001 | 0x1195 | Y | 0x8001 | 0x1195 | Y | 0x8001 | 0x1195 | Y | 0x8001 | 0x1195 | Y | 0x8001 | 0x1195 | Y | 0x8001 | 0x1195 | Y | 0x8001 | 0x1195 | Y | 0x8001 | 0x1195 | Y | 0x8001 | 0x1195 | Y | 0x8001 | 0x1195 | Y | 0x8001 | 0x1195 | Y | 0x8001 | 0x1195 | Y | 0x8001 | 0x1195 | Y | 0x8001 | 0x1195 | Y | 0x8001 | 0x1195 | Y | 0x8001 | 0x1195 | Y | 0x8001 | 0x1195 | Y | 0x8001 | 0x1195
Software entire version | N/A | 0x0013~0x0020 | String | 28 | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | Y | Y | Y | Y | Y | N | 0x8001 | 0x1174 | Y | 0x2016 | 0x1174 | Y | 0x2016 | 0x1174 | Y | 0x2016 | 0x1174 | N | 0x8001 | 0x1174 | Y | 0x2016 | 0x1174 | Y | 0x2016 | 0x1174 | Y | 0x2016 | 0x1174 | Y | 0x8001 | 0x1174 | N | 0x8001 | 0x1174 | Y | 0x2016 | 0x1174 | Y | 0x2016 | 0x1174 | Y | 0x2016 | 0x1174 | N | 0x8001 | 0x1174 | Y | 0x2016 | 0x1174 | Y | 0x2016 | 0x1174 | N | 0x8001 | 0x1174 | Y | 0x2016 | 0x1174 | format: VxxxRxxxCxxSPCxxx
Controller type | N/A | 0x0021 | UNIT16 | 2 | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | 0x8001 | 0x19BF | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N
Device ID | N/A | 0x0022~0x002A | String | 18 | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | 0x8001 | to add | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N

## Collect Information
Data | Unit | Register Address | Data Type | Number of Bytes | Precision | Remarks | SMU05A V500R001 C30/C50/C60 | SMU02B V300R002 C10/C20 | SMU02B V300R003 C00/C10 | SMU02B V500R001 C00/C10/C20/C30/C50/C60 | SMU02B V500R002 C00 | SMU02B V500R003 C10 | SCC800 V100R001C90 | SMU11D V500R002C50 | SMU V500R003C00(DPS) | SMU11B V500R003 C00 | SMU V500R003C10(DPS) | SMU11B V500R003 C10 | iSitePower V100R021C10(DPS) | iSitePower V100R021C10 (SMU02C/02X) | iSitePower V100R021C10 (SMU11B) | iSitePower V100R021C10 (Solar cabinet) | iSitePower V100R021C91 (SMU02C/02X) | iSitePower V100R021C91 (PC510-IOT) | iSitePower V100R021C80 (SMU02C/02X) | DP-SP V300R022C00(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C00(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C00(SMU02C/02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C00 (SMU11B) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(SMU02C/02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10 (SMU11B) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(PVPU) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C00(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C00(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C00(SMU02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | iSitePower V100R023C92(SMU02C/02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C10(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C00(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C00(SMU02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C10(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C10(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C10(SMU02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value)
System DC Voltage | V | 0x1000 | UINT16 | 2 | 1 | Reports the DC voltage of the current cabinet. | Y | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x1101 | Y | 0x8001 | 0x1101 | Y | 0x8001 | 0x1101 | Y | 0x8226 | 0x1101 | Y | 0x8001 | 0x1101 | Y | 0x8001 | 0x1101 | Y | 0x8001 | 0x1101 | Y | 0x8226 | 0x1101 | Y | 0x8001 | 0x1101 | Y | 0x8001 | 0x1101 | Y | 0x8001 | 0x1101 | Y | 0x8001 | 0x1101 | Y | 0x8001 | 0x1101 | Y | 0x8001 | 0x1101 | Y | 0x8001 | 0x1101 | Y | 0x8001 | 0x1101 | Y | 0x8001 | 0x1101 | Y | 0x8001 | 0x1101 | Y | 0x8001 | 0x1101
Total DC Load Current | A | 0x1001 | UINT16 | 2 | 1 | Summarizes the total current of all loads at the system level. | Y | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x1102 | Y | 0x8001 | 0x1102 | Y | 0x8001 | 0x1102 | Y | 0x8001 | 0x1102 | Y | 0x8001 | 0x1102 | Y | 0x8001 | 0x1102 | Y | 0x8001 | 0x1102 | Y | 0x8001 | 0x1102 | Y | 0x8001 | 0x1102 | Y | 0x8001 | 0x1102 | Y | 0x8001 | 0x1102 | Y | 0x8001 | 0x1102 | Y | 0x8001 | 0x1102 | Y | 0x8001 | 0x1102 | Y | 0x8001 | 0x1102 | Y | 0x8001 | 0x1102 | Y | 0x8001 | 0x1102 | Y | 0x8001 | 0x1102 | Y | 0x8001 | 0x1102
Load Shunt 1 Current | A | 0x1002 | UINT16 | 2 | 1 |  | N | Y | Y | Y | Y | Y | N | N |  | Y |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8226 | 0x125F | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x125F | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x125F | Y | 0x8226 | 0x125F | N |  |  | N |  |  | Y | 0x8226 | 0x125F | N |  |  | N |  |  | Y | 0x8226 | 0x125F
Load Shunt 2 Current | A | 0x1003 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AC Voltage | V | 0x1004 | UINT16 | 2 | 1 |  | N | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x1103 | Y | 0x8231 | 0x1103 | Y | 0x8231 | 0x1103 | Y | 0x8231 | 0x1103 | Y | 0x8001 | 0x1103 | Y | 0x8231 | 0x1103 | Y | 0x8231 | 0x1103 | Y | 0x8231 | 0x1103 | N |  |  | Y | 0x8001 | 0x1103 | Y | 0x8231 | 0x1103 | Y | 0x8231 | 0x1103 | Y | 0x8231 | 0x1103 | Y | 0x8231 | 0x1103 | Y | 0x8001 | 0x1103 | Y | 0x8231 | 0x1103 | Y | 0x8231 | 0x1103 | Y | 0x8001 | 0x1103 | Y | 0x8231 | 0x1103
AC Current | A | 0x1005 | UINT16 | 2 | 1 |  | N | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x1132 | Y | 0x8231 | 0x1132 | Y | 0x8231 | 0x1132 | Y | 0x8231 | 0x1132 | Y | 0x8001 | 0x1132 | Y | 0x8231 | 0x1132 | Y | 0x8231 | 0x1132 | Y | 0x8231 | 0x1132 | N |  |  | Y | 0x8001 | 0x1132 | Y | 0x8231 | 0x1132 | Y | 0x8231 | 0x1132 | Y | 0x8231 | 0x1132 | Y | 0x8231 | 0x1132 | Y | 0x8001 | 0x1132 | Y | 0x8231 | 0x1132 | Y | 0x8231 | 0x1132 | Y | 0x8001 | 0x1132 | Y | 0x8231 | 0x1132
Phase L1/Line L1L2Voltage | V | 0x1006 | UINT16 | 2 | 1 | Reports the phase L1/Line L1L2 AC voltage of the current cabinet. If the system is single-phase, reports the system AC voltage. | Y | Y | Y | Y | Y | Y | N | Y |  | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x1262 | Y | 0x8231 | 0x14A9 | Y | 0x8231 | 0x14A9 | Y | 0x8231 | 0x14A9 | Y | 0x8001 | 0x1262 | Y | 0x8231 | 0x14A9 | Y | 0x8231 | 0x14A9 | Y | 0x8231 | 0x14A9 | N |  |  | Y | 0x8001 | 0x1262 | Y | 0x8231 | 0x14A9 | Y | 0x8231 | 0x14A9 | Y | 0x8231 | 0x14A9 | Y | 0x8231 | 0x14A9 | Y | 0x8001 | 0x1262 | Y | 0x8231 | 0x14A9 | Y | 0x8231 | 0x14A9 | Y | 0x8001 | 0x1262 | Y | 0x8231 | 0x14A9
Phase L2/Line L2L3 Voltage | V | 0x1007 | UINT16 | 2 | 1 | Reports the phase L2/Line L2L3 AC voltage of the current cabinet. | Y | Y | Y | Y | Y | Y | N | Y |  | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x1263 | Y | 0x8231 | 0x14AA | Y | 0x8231 | 0x14AA | Y | 0x8231 | 0x14AA | Y | 0x8001 | 0x1263 | Y | 0x8231 | 0x14AA | Y | 0x8231 | 0x14AA | Y | 0x8231 | 0x14AA | N |  |  | Y | 0x8001 | 0x1263 | Y | 0x8231 | 0x14AA | Y | 0x8231 | 0x14AA | Y | 0x8231 | 0x14AA | Y | 0x8231 | 0x14AA | Y | 0x8001 | 0x1263 | Y | 0x8231 | 0x14AA | Y | 0x8231 | 0x14AA | Y | 0x8001 | 0x1263 | Y | 0x8231 | 0x14AA
Phase L3/Line L3L1 Voltage | V | 0x1008 | UINT16 | 2 | 1 | Reports the phase L3/Line L3L1 AC voltage of the current cabinet. | Y | Y | Y | Y | Y | Y | N | Y |  | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x1264 | Y | 0x8231 | 0x14AB | Y | 0x8231 | 0x14AB | Y | 0x8231 | 0x14AB | Y | 0x8001 | 0x1264 | Y | 0x8231 | 0x14AB | Y | 0x8231 | 0x14AB | Y | 0x8231 | 0x14AB | N |  |  | Y | 0x8001 | 0x1264 | Y | 0x8231 | 0x14AB | Y | 0x8231 | 0x14AB | Y | 0x8231 | 0x14AB | Y | 0x8231 | 0x14AB | Y | 0x8001 | 0x1264 | Y | 0x8231 | 0x14AB | Y | 0x8231 | 0x14AB | Y | 0x8001 | 0x1264 | Y | 0x8231 | 0x14AB
Phase L1 Current | A | 0x1009 | UINT16 | 2 | 1 | Reports the phase L1 AC current of the current cabinet. If the system is single-phase, reports the system AC current. | Y | Y | Y | Y | Y | Y | N | Y |  | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x1136 | Y | 0x8231 | 0x14AC | Y | 0x8231 | 0x14AC | Y | 0x8231 | 0x14AC | Y | 0x8001 | 0x1136 | Y | 0x8231 | 0x14AC | Y | 0x8231 | 0x14AC | Y | 0x8231 | 0x14AC | N |  |  | Y | 0x8001 | 0x1136 | Y | 0x8231 | 0x14AC | Y | 0x8231 | 0x14AC | Y | 0x8231 | 0x14AC | Y | 0x8231 | 0x14AC | Y | 0x8001 | 0x1136 | Y | 0x8231 | 0x14AC | Y | 0x8231 | 0x14AC | Y | 0x8001 | 0x1136 | Y | 0x8231 | 0x14AC
Phase L2 Current | A | 0x100A | UINT16 | 2 | 1 | Reports the phase L2 AC current of the current cabinet. | Y | Y | Y | Y | Y | Y | N | Y |  | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x1137 | Y | 0x8231 | 0x14AD | Y | 0x8231 | 0x14AD | Y | 0x8231 | 0x14AD | Y | 0x8001 | 0x1137 | Y | 0x8231 | 0x14AD | Y | 0x8231 | 0x14AD | Y | 0x8231 | 0x14AD | N |  |  | Y | 0x8001 | 0x1137 | Y | 0x8231 | 0x14AD | Y | 0x8231 | 0x14AD | Y | 0x8231 | 0x14AD | Y | 0x8231 | 0x14AD | Y | 0x8001 | 0x1137 | Y | 0x8231 | 0x14AD | Y | 0x8231 | 0x14AD | Y | 0x8001 | 0x1137 | Y | 0x8231 | 0x14AD
Phase L3 Current | A | 0x100B | UINT16 | 2 | 1 | Reports the phase L3 AC current of the current cabinet. | Y | Y | Y | Y | Y | Y | N | Y |  | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x1138 | Y | 0x8231 | 0x14AE | Y | 0x8231 | 0x14AE | Y | 0x8231 | 0x14AE | Y | 0x8001 | 0x1138 | Y | 0x8231 | 0x14AE | Y | 0x8231 | 0x14AE | Y | 0x8231 | 0x14AE | N |  |  | Y | 0x8001 | 0x1138 | Y | 0x8231 | 0x14AE | Y | 0x8231 | 0x14AE | Y | 0x8231 | 0x14AE | Y | 0x8231 | 0x14AE | Y | 0x8001 | 0x1138 | Y | 0x8231 | 0x14AE | Y | 0x8231 | 0x14AE | Y | 0x8001 | 0x1138 | Y | 0x8231 | 0x14AE
AC Frequency | Hz | 0x100C | UINT16 | 2 | 0 | Reports the AC frequency of the current cabinet. | Y | Y | Y | Y | Y | Y | N | N | Y | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x1221 | Y | 0x8231 | 0x1822 | Y | 0x8231 | 0x1822 | Y | 0x8231 | 0x1822 | Y | 0x8001 | 0x1221 | Y | 0x8231 | 0x1822 | Y | 0x8231 | 0x1822 | Y | 0x8231 | 0x1822 | N |  |  | Y | 0x8001 | 0x1221 | Y | 0x8231 | 0x1822 | Y | 0x8231 | 0x1822 | Y | 0x8231 | 0x1822 | Y | 0x8231 | 0x1822 | Y | 0x8001 | 0x1221 | Y | 0x8231 | 0x1822 | Y | 0x8231 | 0x1822 | Y | 0x8001 | 0x1221 | Y | 0x8231 | 0x1822
Equipment Area Temperature | degC | 0x100D | INT16 | 2 | 0 | Summarizes the maximum ambient temperature. | Y | Y | Y | Y | Y | Y | N | N |  | Y |  | Y |  | Y | Y | Y | Y | N | Y | N |  |  | N |  |  | Y | 0x9032 | 0x1113 | Y | 0x9032 | 0x1113 | N |  |  | N |  |  | Y | 0x9032 | 0x1113 | Y | 0x9032 | 0x1113 | N |  |  | N |  |  | N |  |  | Y | 0x9032 | 0x1113 | Y | 0x9032 | 0x1113 | N |  |  | N |  |  | Y | 0x9032 | 0x1113 | N |  |  | N |  |  | Y | 0x9032 | 0x1113
Ambient Humidity | % | 0x100E | UINT16 | 2 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | Y |  | N |  | Y | N | Y | Y | N | Y | N |  |  | N |  |  | Y | 0x9032 | 0x1114 | N |  |  | N |  |  | N |  |  | Y | 0x9032 | 0x1114 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9032 | 0x1114 | Y | 0x9032 | 0x1114 | N |  |  | N |  |  | Y | 0x9032 | 0x1114 | N |  |  | N |  |  | Y | 0x9032 | 0x1114
DC Input Voltage | V | 0x100F | UINT16 | 2 | 1 | [9 empty] | Y | N | Y | N | Y |  | N |  |  | N |  | Y | 0x8001 | 0x1490 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1490 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1490 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1490 | N |  |  | N |  |  | Y | 0x8001 | 0x1490 | N
DC Input Current | A | 0x1010 | UINT16 | 2 | 1 | [9 empty] | Y | N | Y | N | Y |  | N |  |  | N |  | Y | 0x8001 | 0x1491 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1491 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1491 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1491 | N |  |  | N |  |  | Y | 0x8001 | 0x1491 | N
Battery Branch Current | A | 0x1011 | INT16 | 2 | 1 | [8 empty] | Y |  | N |  | N |  |  | N |  |  | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Mains Power Consumption | kWh | 0x1012~0x1013 | UINT32 | 4 | 2 | [8 empty] | Y |  | N |  | N |  |  | N |  |  | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DC Load Power Consumption | kWh | 0x1014~0x1015 | UINT32 | 4 | 2 | [8 empty] | Y |  | N |  | N |  |  | N |  |  | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Rectifier N Type (N:1~12) | NA | 0x1016+(N-1) | UINT16 | 2 | 0 | 0:5G Rectifier 1:Not 5G Rectifier | [7 empty] | Y |  | N |  | N |  |  | N |  |  | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers Reserved(0x1022~0x102D) | [13 empty] | N |  | N |  |  | N |  |  |  |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
UIM Temp1 Temperature | degC | 0x102E | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
UIM Temp2 Temperature | degC | 0x102F | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AC Voltage | V | 0x1030 | UINT16 | 2 | 1 | AC2 | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x1103 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1103 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1103 | Y | 0x8231 | 0x1103 | N |  |  | N |  |  | Y | 0x8231 | 0x1103 | N |  |  | N |  |  | Y | 0x8231 | 0x1103
AC Current | A | 0x1031 | UINT16 | 2 | 1 | AC2 | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x1132 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1132 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1132 | Y | 0x8231 | 0x1132 | N |  |  | N |  |  | Y | 0x8231 | 0x1132 | N |  |  | N |  |  | Y | 0x8231 | 0x1132
Phase L1/Line L1L2Voltage | V | 0x1032 | UINT16 | 2 | 1 | AC2 Reports the phase L1/Line L1L2 AC voltage of the current cabinet. If the system is single-phase, reports the system AC voltage. | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x14A9 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14A9 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14A9 | Y | 0x8231 | 0x14A9 | N |  |  | N |  |  | Y | 0x8231 | 0x14A9 | N |  |  | N |  |  | Y | 0x8231 | 0x14A9
Phase L2/Line L2L3 Voltage | V | 0x1033 | UINT16 | 2 | 1 | AC2 Reports the phase L2/Line L2L3 AC voltage of the current cabinet. | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x14AA | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AA | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AA | Y | 0x8231 | 0x14AA | N |  |  | N |  |  | Y | 0x8231 | 0x14AA | N |  |  | N |  |  | Y | 0x8231 | 0x14AA
Phase L3/Line L3L1 Voltage | V | 0x1034 | UINT16 | 2 | 1 | AC2 Reports the phase L3/Line L3L1 AC voltage of the current cabinet. | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x14AB | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AB | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AB | Y | 0x8231 | 0x14AB | N |  |  | N |  |  | Y | 0x8231 | 0x14AB | N |  |  | N |  |  | Y | 0x8231 | 0x14AB
Phase L1 Current | A | 0x1035 | UINT16 | 2 | 1 | AC2 Reports the phase L1 AC current of the current cabinet. If the system is single-phase, reports the system AC current. | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x14AC | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AC | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AC | Y | 0x8231 | 0x14AC | N |  |  | N |  |  | Y | 0x8231 | 0x14AC | N |  |  | N |  |  | Y | 0x8231 | 0x14AC
Phase L2 Current | A | 0x1036 | UINT16 | 2 | 1 | AC2 Reports the phase L2 AC current of the current cabinet. | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x14AD | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AD | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AD | Y | 0x8231 | 0x14AD | N |  |  | N |  |  | Y | 0x8231 | 0x14AD | N |  |  | N |  |  | Y | 0x8231 | 0x14AD
Phase L3 Current | A | 0x1037 | UINT16 | 2 | 1 | AC2 Reports the phase L3 AC current of the current cabinet. | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x14AE | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AE | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AE | Y | 0x8231 | 0x14AE | N |  |  | N |  |  | Y | 0x8231 | 0x14AE | N |  |  | N |  |  | Y | 0x8231 | 0x14AE
AC Frequency | Hz | 0x1038 | UINT16 | 2 | 0 | AC2 Reports the AC frequency of the current cabinet. | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x1822 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1822 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1822 | Y | 0x8231 | 0x1822 | N |  |  | N |  |  | Y | 0x8231 | 0x1822 | N |  |  | N |  |  | Y | 0x8231 | 0x1822
DC Load1 Voltage | V | 0x1039 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1830 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1830 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1830 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1830 | N |  |  | N |  |  | Y | 0x8001 | 0x1830 | N
DC Load2 Voltage | V | 0x103A | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1831 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1831 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1831 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1831 | N |  |  | N |  |  | Y | 0x8001 | 0x1831 | N
DC Load3 Voltage | V | 0x103B | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1832 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1832 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1832 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1832 | N |  |  | N |  |  | Y | 0x8001 | 0x1832 | N
DC Load4 Voltage | V | 0x103C | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1833 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1833 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1833 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1833 | N |  |  | N |  |  | Y | 0x8001 | 0x1833 | N
DC Load5 Voltage | V | 0x103D | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1834 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1834 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1834 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1834 | N |  |  | N |  |  | Y | 0x8001 | 0x1834 | N
DC Load6 Voltage | V | 0x103E | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1835 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1835 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1835 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1835 | N |  |  | N |  |  | Y | 0x8001 | 0x1835 | N
DC Load7 Voltage | V | 0x103F | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1836 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1836 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1836 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1836 | N |  |  | N |  |  | Y | 0x8001 | 0x1836 | N
DC Load1 Current | A | 0x1040 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x138E | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x138E | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x138E | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x138E | N |  |  | N |  |  | Y | 0x8001 | 0x138E | N
DC Load2 Current | A | 0x1041 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x138F | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x138F | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x138F | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x138F | N |  |  | N |  |  | Y | 0x8001 | 0x138F | N
DC Load3 Current | A | 0x1042 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1390 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1390 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1390 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1390 | N |  |  | N |  |  | Y | 0x8001 | 0x1390 | N
DC Load4 Current | A | 0x1043 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1391 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1391 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1391 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1391 | N |  |  | N |  |  | Y | 0x8001 | 0x1391 | N
DC Load5 Current | A | 0x1044 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1392 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1392 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1392 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1392 | N |  |  | N |  |  | Y | 0x8001 | 0x1392 | N
DC Load6 Current | A | 0x1045 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1393 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1393 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1393 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1393 | N |  |  | N |  |  | Y | 0x8001 | 0x1393 | N
DC Load7 Current | A | 0x1046 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1394 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1394 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1394 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1394 | N |  |  | N |  |  | Y | 0x8001 | 0x1394 | N
DC Load1 Power | kW | 0x1047 | UINT16 | 2 | 2 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1521 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1521 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1521 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1521 | N |  |  | N |  |  | Y | 0x8001 | 0x1521 | N
DC Load2 Power | kW | 0x1048 | UINT16 | 2 | 2 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1522 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1522 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1522 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1522 | N |  |  | N |  |  | Y | 0x8001 | 0x1522 | N
DC Load3 Power | kW | 0x1049 | UINT16 | 2 | 2 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1523 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1523 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1523 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1523 | N |  |  | N |  |  | Y | 0x8001 | 0x1523 | N
DC Load4 Power | kW | 0x104A | UINT16 | 2 | 2 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1524 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1524 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1524 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1524 | N |  |  | N |  |  | Y | 0x8001 | 0x1524 | N
DC Load5 Power | kW | 0x104B | UINT16 | 2 | 2 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1525 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1525 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1525 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1525 | N |  |  | N |  |  | Y | 0x8001 | 0x1525 | N
DC Load6 Power | kW | 0x104C | UINT16 | 2 | 2 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1526 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1526 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1526 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1526 | N |  |  | N |  |  | Y | 0x8001 | 0x1526 | N
DC Load7 Power | kW | 0x104D | UINT16 | 2 | 2 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1527 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1527 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1527 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1527 | N |  |  | N |  |  | Y | 0x8001 | 0x1527 | N
DC Load Number | NA | 0x104E | UINT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x2038 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2038 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2038 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2038 | N |  |  | N |  |  | Y | 0x8001 | 0x2038 | N
User Customize QR CODE | NA | 0x104F~0x105E | String | 32 | 0 | DPS： QR code customized by Rakuten in Japan | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x183A | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x183A | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x183A | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x183A | N |  |  | N |  |  | Y | 0x8001 | 0x183A | N
DC Load1 Contactor Status | NA | 0x1060 | UINT16 | 2 | 0 | [close=0]/[open=1] | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1915 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1915 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1915 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1915 | N |  |  | N |  |  | Y | 0x8001 | 0x1915 | N
DC Load2 Contactor Status | NA | 0x1061 | UINT16 | 2 | 0 | [close=0]/[open=1] | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1916 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1916 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1916 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1916 | N |  |  | N |  |  | Y | 0x8001 | 0x1916 | N
DC Load3 Contactor Status | NA | 0x1062 | UINT16 | 2 | 0 | [close=0]/[open=1] | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1917 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1917 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1917 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1917 | N |  |  | N |  |  | Y | 0x8001 | 0x1917 | N
DC Load4 Contactor Status | NA | 0x1063 | UINT16 | 2 | 0 | [close=0]/[open=1] | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1918 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1918 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1918 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1918 | N |  |  | N |  |  | Y | 0x8001 | 0x1918 | N
DC Load5 Contactor Status | NA | 0x1064 | UINT16 | 2 | 0 | [close=0]/[open=1] | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x1919 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1919 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1919 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x1919 | N |  |  | N |  |  | Y | 0x8001 | 0x1919 | N
DC Load6 Contactor Status | NA | 0x1065 | UINT16 | 2 | 0 | [close=0]/[open=1] | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x191A | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x191A | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x191A | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x191A | N |  |  | N |  |  | Y | 0x8001 | 0x191A | N
DC Load7 Contactor Status | NA | 0x1066 | UINT16 | 2 | 0 | [close=0]/[open=1] | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N | N | N | N | N | Y | 0x8001 | 0x191B | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x191B | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x191B | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x191B | N |  |  | N |  |  | Y | 0x8001 | 0x191B | N
|  | Registers Reserved(0x1080~10FF) | [23 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Rectifier Total Output Current | A | 0x1100 | UINT16 | 2 | 1 | Summarizes the total output current of all modules at the system level. | Y | Y | Y | Y | Y | Y | N | N | Y | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8003 | 0x1001 | Y | 0x8003 | 0x1001 | Y | 0x8003 | 0x1001 | Y | 0x8003 | 0x1001 | Y | 0x8003 | 0x1001 | Y | 0x8003 | 0x1001 | Y | 0x8003 | 0x1001 | Y | 0x8003 | 0x1001 | N |  |  | Y | 0x8003 | 0x1001 | Y | 0x8003 | 0x1001 | Y | 0x8003 | 0x1001 | Y | 0x8003 | 0x1001 | Y | 0x8003 | 0x1001 | Y | 0x8003 | 0x1001 | Y | 0x8003 | 0x1001 | Y | 0x8003 | 0x1001 | Y | 0x8003 | 0x1001 | Y | 0x8003 | 0x1001
Rectifier Amount |  | 0x1101 | UINT16 | 2 | 0 | Summarizes the number of all modules at the system level. | Y | Y | Y | Y | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | Y | 0x8003 | 0x1012 | Y | 0x8003 | 0x1012 | Y | 0x8003 | 0x1012 | N |  |  | Y | 0x8003 | 0x1012 | Y | 0x8003 | 0x1012 | Y | 0x8003 | 0x1012 | N |  |  | N |  |  | Y | 0x8003 | 0x1012 | Y | 0x8003 | 0x1012 | Y | 0x8003 | 0x1012 | Y | 0x8003 | 0x1012 | N |  |  | Y | 0x8003 | 0x1012 | Y | 0x8003 | 0x1012 | N |  |  | Y | 0x8003 | 0x1012
Rectifier Total DC Power | W | 0x1102~0x1103 | UINT32 | 4 | 0 |  | N | Y | Y | Y | Y | Y | N | N | Y | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8003 | 0x100D | Y | 0x8003 | 0x100D | Y | 0x8003 | 0x100D | Y | 0x8003 | 0x100D | Y | 0x8003 | 0x100D | Y | 0x8003 | 0x100D | Y | 0x8003 | 0x100D | Y | 0x8003 | 0x100D | N |  |  | Y | 0x8003 | 0x100D | Y | 0x8003 | 0x100D | Y | 0x8003 | 0x100D | Y | 0x8003 | 0x100D | Y | 0x8003 | 0x100D | Y | 0x8003 | 0x100D | Y | 0x8003 | 0x100D | Y | 0x8003 | 0x100D | Y | 0x8003 | 0x100D | Y | 0x8003 | 0x100D
|  | Registers Reserved(0x1104~0x110F) | [11 empty] | N | [11 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Rectifier N DC Output Current (N:1~60) | A | 0x1110+(N-1) | UINT16 | 2 | 1 | the max value N is 60. | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers Reserved(0x114c~0x114F) | [23 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Rectifier N Turn On/Off Status (N:1~60) | NA | 0x1150+(N-1) | UINT16 | 2 | 0 | the max value N is 60. [On=0]/[Off=1] | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers Reserved(0x118c~0x11FF) | [23 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Phase L1 Active Power | kW | 0x1200~0x1201 | INT32 | 4 | 2 | [18 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Phase L2 Active Power | kW | 0x1202~0x1203 | INT32 | 4 | 2 | [18 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Phase L3 Active Power | kW | 0x1204~0x1205 | INT32 | 4 | 2 | [18 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Phase L1 Reactive Power | Kvar | 0x1206~0x1207 | INT32 | 4 | 2 | [18 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Phase L2 Reactive Power | Kvar | 0x1208~0x1209 | INT32 | 4 | 2 | [18 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Phase L3 Reactive Power | Kvar | 0x120A~0x120B | INT32 | 4 | 2 | [18 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Phase L1 Power Factor | NA | 0x120C | INT16 | 2 | 2 | [18 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Phase L2 Power Factor | NA | 0x120D | INT16 | 2 | 2 | [18 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Phase L3 Power Factor | NA | 0x120E | INT16 | 2 | 2 | [18 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Active Power | kW | 0x120F~0x1210 | INT32 | 4 | 2 | [18 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Reactive Power | Kvar | 0x1211~0x1212 | INT32 | 4 | 2 | [18 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Total Power Factor | NA | 0x1213 | INT16 | 2 | 2 | [18 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AC Frequency | Hz | 0x1214 | UINT16 | 2 | 2 | [18 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers Reserved For AC Meter(0x12xx~0x12FF) | [23 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Battery Status | NA | 0x1400 | UINT16 | 2 | 0 | System-level summary 0: float charging; 1: equalized charging; 2: discharge; 3. hibernation | Y | Y | Y | Y | Y | Y | N | Y |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x1055 | Y | 0x8004 | 0x1055 | N |  |  | N |  |  | Y | 0x8004 | 0x1055 | Y | 0x8004 | 0x1055 | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x1055 | Y | 0x8004 | 0x1055 | N |  |  | N |  |  | Y | 0x8004 | 0x1055 | N |  |  | N |  |  | Y | 0x8004 | 0x1055
Total Battery Current | A | 0x1401 | INT16 | 2 | 1 | Summarizes the currents of all batteries at the system level. | Y | Y | Y | Y | Y | Y | N | Y |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x1029 | Y | 0x8004 | 0x1029 | N |  |  | N |  |  | Y | 0x8004 | 0x1029 | Y | 0x8004 | 0x1029 | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x1029 | Y | 0x8004 | 0x1029 | N |  |  | N |  |  | Y | 0x8004 | 0x1029 | N |  |  | N |  |  | Y | 0x8004 | 0x1029
Total Remaining Capacity Percent | % | 0x1402 | UINT16 | 2 | 0 | System-level summary | Y | Y | Y | Y | Y | Y | N | Y |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x10BF | Y | 0x8004 | 0x10BF | N |  |  | N |  |  | Y | 0x8004 | 0x10BF | Y | 0x8004 | 0x10BF | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x10BF | Y | 0x8004 | 0x10BF | N |  |  | N |  |  | Y | 0x8004 | 0x10BF | N |  |  | N |  |  | Y | 0x8004 | 0x10BF
Battery 1 Temperature | degC | 0x1403 | INT16 | 2 | 0 | System-level summary | Y | Y | Y | Y | Y | Y | N | Y |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x110C | Y | 0x8004 | 0x1001 | N |  |  | N |  |  | Y | 0x8004 | 0x110C | Y | 0x8004 | 0x1001 | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x110C | Y | 0x8004 | 0x110C | N |  |  | N |  |  | Y | 0x8004 | 0x110C | N |  |  | N |  |  | Y | 0x8004 | 0x110C
Battery Amount | NA | 0x1404 | UINT16 | 2 | 0 | System-level summary | Y | Y | Y | Y | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x2001 | Y | 0x8004 | 0x2001 | N |  |  | N |  |  | Y | 0x8004 | 0x2001 | Y | 0x8004 | 0x2001 | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x2001 | Y | 0x8004 | 0x2001 | N |  |  | N |  |  | Y | 0x8004 | 0x2001 | N |  |  | N |  |  | Y | 0x8004 | 0x2001
Battery N Terminal Voltage N:1-4 | V | 0x1405+(N-1) | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers Reserved | [23 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Ambient Temperature | degC | 0x1500 | INT16 | 2 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x800B | 0x1002 | Y | 0x8083 | 0x1113 | N |  |  | N |  |  | Y | 0x800B | 0x1002 | Y | 0x8083 | 0x1113 | N |  |  | N |  |  | N |  |  | Y | 0x800B | 0x1002 | Y | 0x800B | 0x1002 | N |  |  | N |  |  | Y | 0x800B | 0x1002 | N |  |  | N |  |  | Y | 0x800B | 0x1002
System Input Type | NA | 0x1501 | UINT16 | 2 | 0 | 0-AC Input 1-DC Input | [8 empty] | Y |  | Y |  | Y | [6 empty] | Y | 0x8001 | 0x2535 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2535 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2535 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2535 | N |  |  | N |  |  | Y | 0x8001 | 0x2535 | N
|  | Registers Reserved | [11 empty] | N | [9 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Fan 1 Speed | RPM | 0x1530 | UINT16 | 2 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x800C | 0x1002 | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x1002 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x1002 | Y | 0x800C | 0x1002 | N |  |  | N |  |  | Y | 0x800C | 0x1002 | N |  |  | N |  |  | Y | 0x800C | 0x1002
Fan 2 Speed | RPM | 0x1531 | UINT16 | 2 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x800C | 0x1004 | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x1004 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x1004 | Y | 0x800C | 0x1004 | N |  |  | N |  |  | Y | 0x800C | 0x1004 | N |  |  | N |  |  | Y | 0x800C | 0x1004
Fan 3 Speed | RPM | 0x1532 | UINT16 | 2 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x800C | 0x1006 | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x1006 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x1006 | Y | 0x800C | 0x1006 | N |  |  | N |  |  | Y | 0x800C | 0x1006 | N |  |  | N |  |  | Y | 0x800C | 0x1006
Fan 4 Speed | RPM | 0x1533 | UINT16 | 2 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x800C | 0x1008 | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x1008 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x1008 | Y | 0x800C | 0x1008 | N |  |  | N |  |  | Y | 0x800C | 0x1008 | N |  |  | N |  |  | Y | 0x800C | 0x1008
Fan Amount | NA | 0x1534 | UINT16 | 2 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x800C | 0x2001 | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x2001 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x2001 | Y | 0x800C | 0x2001 | N |  |  | N |  |  | Y | 0x800C | 0x2001 | N |  |  | N |  |  | Y | 0x800C | 0x2001
|  | Registers Reserved | [23 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Air Conditioner 1 Running Status | NA | 0x1560 | UINT16 | 2 | 0 | 1:Standby 2:Running 3:Fault | N | Y | Y | Y | Y | Y | N | N |  | Y |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8009 | 0x1001 | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x1001 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x1001 | Y | 0x8009 | 0x1001 | N |  |  | N |  |  | Y | 0x8009 | 0x1001 | N |  |  | N |  |  | Y | 0x8009 | 0x1001
Air Conditioner 1 Compressor status | NA | 0x1561 | UINT16 | 2 | 0 | 1:Standby 2:Running 3:Fault | N | Y | Y | Y | Y | Y | N | N |  | Y |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8009 | 0x1002 | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x1002 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x1002 | Y | 0x8009 | 0x1002 | N |  |  | N |  |  | Y | 0x8009 | 0x1002 | N |  |  | N |  |  | Y | 0x8009 | 0x1002
Air Conditioner 1 Internal Fan Speed | RPM | 0x1562 | UINT16 | 2 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | Y |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8009 | 0x1007 | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x1007 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x1007 | Y | 0x8009 | 0x1007 | N |  |  | N |  |  | Y | 0x8009 | 0x1007 | N |  |  | N |  |  | Y | 0x8009 | 0x1007
Air Conditioner 1 External Fan Speed | RPM | 0x1563 | UINT16 | 2 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | Y |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8009 | 0x1008 | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x1008 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x1008 | Y | 0x8009 | 0x1008 | N |  |  | N |  |  | Y | 0x8009 | 0x1008 | N |  |  | N |  |  | Y | 0x8009 | 0x1008
Air Conditioner 1 Runtime | h | 0x1564 | UINT32 | 4 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | Y |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8009 | 0x1010 | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x1010 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x1010 | Y | 0x8009 | 0x1010 | N |  |  | N |  |  | Y | 0x8009 | 0x1010 | N |  |  | N |  |  | Y | 0x8009 | 0x1010
Air Conditioner 1 Compressor Runtime | h | 0x1566 | UINT32 | 4 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | Y |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8009 | 0x1011 | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x1011 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x1011 | Y | 0x8009 | 0x1011 | N |  |  | N |  |  | Y | 0x8009 | 0x1011 | N |  |  | N |  |  | Y | 0x8009 | 0x1011
|  | Registers(0x1567~0x157F) Reserved for Air conditioner |  |  |  |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
|  | Registers Reserved | [23 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Battery Cabinet Area Temperature | degC | 0x1600 | INT16 | 2 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x1002 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1002 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1002 | Y | 0x8022 | 0x1002 | N |  |  | N |  |  | Y | 0x8022 | 0x1002 | N |  |  | N |  |  | Y | 0x8022 | 0x1002
Battery 2 Temperature | degC | 0x1601 | INT16 | 2 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x1003 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1003 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1003 | Y | 0x8022 | 0x1003 | N |  |  | N |  |  | Y | 0x8022 | 0x1003 | N |  |  | N |  |  | Y | 0x8022 | 0x1003
Air Conditioner 2 Running Status | NA | 0x1602 | UINT16 | 2 | 0 | 1:Standby 2:Running 3:Fault | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x1011 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1011 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1011 | Y | 0x8022 | 0x1011 | N |  |  | N |  |  | Y | 0x8022 | 0x1011 | N |  |  | N |  |  | Y | 0x8022 | 0x1011
Air Conditioner 2 Compressor status | NA | 0x1603 | UINT16 | 2 | 0 | 1:Standby 2:Running 3:Fault | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x1012 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1012 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1012 | Y | 0x8022 | 0x1012 | N |  |  | N |  |  | Y | 0x8022 | 0x1012 | N |  |  | N |  |  | Y | 0x8022 | 0x1012
Air Conditioner 2 Internal Fan Speed | RPM | 0x1604 | UINT16 | 2 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x1013 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1013 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1013 | Y | 0x8022 | 0x1013 | N |  |  | N |  |  | Y | 0x8022 | 0x1013 | N |  |  | N |  |  | Y | 0x8022 | 0x1013
Air Conditioner 2 External Fan Speed | RPM | 0x1605 | UINT16 | 2 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x1014 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1014 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1014 | Y | 0x8022 | 0x1014 | N |  |  | N |  |  | Y | 0x8022 | 0x1014 | N |  |  | N |  |  | Y | 0x8022 | 0x1014
Air Conditioner 2 Runtime | h | 0x1606 | UINT32 | 4 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x1015 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1015 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1015 | Y | 0x8022 | 0x1015 | N |  |  | N |  |  | Y | 0x8022 | 0x1015 | N |  |  | N |  |  | Y | 0x8022 | 0x1015
Air Conditioner 2 Compressor Runtime | h | 0x1608 | UINT32 | 4 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x1016 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1016 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1016 | Y | 0x8022 | 0x1016 | N |  |  | N |  |  | Y | 0x8022 | 0x1016 | N |  |  | N |  |  | Y | 0x8022 | 0x1016
Fan 1 Speed | RPM | 0x160A | UINT16 | 2 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x1006 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1006 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1006 | Y | 0x8022 | 0x1006 | N |  |  | N |  |  | Y | 0x8022 | 0x1006 | N |  |  | N |  |  | Y | 0x8022 | 0x1006
Fan 2 Speed | RPM | 0x160B | UINT16 | 2 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x1007 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1007 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1007 | Y | 0x8022 | 0x1007 | N |  |  | N |  |  | Y | 0x8022 | 0x1007 | N |  |  | N |  |  | Y | 0x8022 | 0x1007
Fan 3 Speed | RPM | 0x160C | UINT16 | 2 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x1008 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1008 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1008 | Y | 0x8022 | 0x1008 | N |  |  | N |  |  | Y | 0x8022 | 0x1008 | N |  |  | N |  |  | Y | 0x8022 | 0x1008
Fan 4 Speed | RPM | 0x160D | UINT16 | 2 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x1009 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1009 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1009 | Y | 0x8022 | 0x1009 | N |  |  | N |  |  | Y | 0x8022 | 0x1009 | N |  |  | N |  |  | Y | 0x8022 | 0x1009
Fan Amount | NA | 0x160E | UINT16 | 2 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x1004 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1004 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x1004 | Y | 0x8022 | 0x1004 | N |  |  | N |  |  | Y | 0x8022 | 0x1004 | N |  |  | N |  |  | Y | 0x8022 | 0x1004
|  | Registers(0x160F~0x161F) Reserved for Air conditioner |  |  |  |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
|  | Registers Reserved | [23 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
DG Amount | NA | 0x16F0 | UINT16 | 2 | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | Y |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9031 | 0x2693 | N |  |  | N |  |  | N |  |  | Y | 0x9031 | 0x2693 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9031 | 0x2693 | Y | 0x9031 | 0x2693 | N |  |  | N |  |  | Y | 0x9031 | 0x2693 | N |  |  | N |  |  | Y | 0x9031 | 0x2693
|  | Registers Reserved | [23 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
DG N Type(N:1–2) | NA | 0x1700+(N-1)*32 | UINT16 |  | NA | 0: Smart 1: Non-intelligent | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Status | NA | 0x1701+(N-1)*32 | UINT16 |  | NA | 0: Stop 1: Running 2: Unknown | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Ua | V | 0x1702+(N-1)*32 | UINT16 |  | 1 |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Ub | V | 0x1703+(N-1)*32 | UINT16 |  | 1 |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Uc | V | 0x1704+(N-1)*32 | UINT16 |  | 1 |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Ia | A | 0x1705+(N-1)*32 | UINT16 |  | 1 |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Ib | A | 0x1706+(N-1)*32 | UINT16 |  | 1 |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Ic | A | 0x1707+(N-1)*32 | UINT16 |  | 1 |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Output Power | kW | 0x1708+(N-1)*32 | UINT16 |  | 1 |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Frequency | Hz | 0x1709+(N-1)*32 | UINT16 |  | 1 |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Battery Voltage | V | 0x170A+(N-1)*32 | UINT16 |  | 1 |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Water Temperature | degC | 0x170B+(N-1)*32 | INT16 |  | 0 |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N RPM | r/min | 0x170C+(N-1)*32 | UINT16 |  | 0 |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Total Fuel Consumption | L | 0x170D+(N-1)*32 | UINT16 |  | 0 |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Total Runtime | h | 0x170E+(N-1)*32 | UINT16 |  | 0 |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Cabin Temperature | degC | 0x170F+(N-1)*32 | INT16 |  | 1 |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Load Rate | % | 0x1710+(N-1)*32 | INT16 |  | 1 |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers Reserved | [23 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
SSU Total Current | A | 0x1800 | UINT16 |  | 1 |  | N | N | N | N | N | N | N | N |  | Y |  | Y |  | Y | Y | Y | Y | N | Y | N |  |  | N |  |  | Y | 0x8011 | 0x1002 | Y | 0x8011 | 0x1002 | N |  |  | N |  |  | Y | 0x8011 | 0x1002 | Y | 0x8011 | 0x1002 | Y | 0x8011 | 0x1002 | N |  |  | N |  |  | Y | 0x8011 | 0x1002 | Y | 0x8011 | 0x1002 | N |  |  | N |  |  | Y | 0x8011 | 0x1002 | N |  |  | N |  |  | Y | 0x8011 | 0x1002
SSU Amount |  | 0x1801 | UINT16 |  | 0 |  | N | Y | Y | Y | Y | Y | N | N |  | Y |  | Y |  | Y | Y | Y | Y | N | Y | N |  |  | N |  |  | Y | 0x8011 | 0x1007 | Y | 0x8011 | 0x1007 | N |  |  | N |  |  | Y | 0x8011 | 0x1007 | Y | 0x8011 | 0x1007 | Y | 0x8011 | 0x1007 | N |  |  | N |  |  | Y | 0x8011 | 0x1007 | Y | 0x8011 | 0x1007 | N |  |  | N |  |  | Y | 0x8011 | 0x1007 | N |  |  | N |  |  | Y | 0x8011 | 0x1007
SSU Total Output Power | kW | 0x1802~0x1803 | UINT32 |  | 2 |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8011 | 0x1005 | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers Reserved | [23 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
SSU 1–N (N=60) Running State | NA | 0x1810+(N-1)*16 | UINT16 |  | NA | 0: ON 1: OFF | N | N | N | N | N | N | N | N |  | N |  | Y |  | Y | Y | Y | Y | N | Y | N |  |  | N |  |  | Y | 0x8012 | 0x1005 | Y | 0x8012 | 0x1005 | N |  |  | N |  |  | Y | 0x8012 | 0x1005 | Y | 0x8012 | 0x1005 | Y | 0x8012 | 0x1005 | N |  |  | N |  |  | Y | 0x8012 | 0x1005 | Y | 0x8012 | 0x1005 | N |  |  | N |  |  | Y | 0x8012 | 0x1005 | N |  |  | N |  |  | Y | 0x8012 | 0x1005
SSU 1–N Input Voltage | V | 0x1811+(N-1)*16 | UINT16 |  | 1 |  | N | N | N | N | N | N | N | N |  | Y |  | Y |  | Y | Y | Y | Y | N | Y | N |  |  | N |  |  | Y | 0x8012 | 0x1004 | Y | 0x8012 | 0x1004 | N |  |  | N |  |  | Y | 0x8012 | 0x1004 | Y | 0x8012 | 0x1004 | Y | 0x8012 | 0x1004 | N |  |  | N |  |  | Y | 0x8012 | 0x1004 | Y | 0x8012 | 0x1004 | N |  |  | N |  |  | Y | 0x8012 | 0x1004 | N |  |  | N |  |  | Y | 0x8012 | 0x1004
SSU 1–N Output Voltage | V | 0x1812+(N-1)*16 | UINT16 |  | 1 |  | N | N | N | N | N | N | N | N |  | Y |  | Y |  | Y | Y | Y | Y | N | Y | N |  |  | N |  |  | Y | 0x8012 | 0x1002 | Y | 0x8012 | 0x1002 | N |  |  | N |  |  | Y | 0x8012 | 0x1002 | Y | 0x8012 | 0x1002 | Y | 0x8012 | 0x1002 | N |  |  | N |  |  | Y | 0x8012 | 0x1002 | Y | 0x8012 | 0x1002 | N |  |  | N |  |  | Y | 0x8012 | 0x1002 | N |  |  | N |  |  | Y | 0x8012 | 0x1002
SSU 1–N Output Current | A | 0x1813+(N-1)*16 | UINT16 |  | 1 |  | N | N | N | N | N | N | N | N |  | Y |  | Y |  | Y | Y | Y | Y | N | Y | N |  |  | N |  |  | Y | 0x8012 | 0x1003 | Y | 0x8012 | 0x1003 | N |  |  | N |  |  | Y | 0x8012 | 0x1003 | Y | 0x8012 | 0x1003 | Y | 0x8012 | 0x1003 | N |  |  | N |  |  | Y | 0x8012 | 0x1003 | Y | 0x8012 | 0x1003 | N |  |  | N |  |  | Y | 0x8012 | 0x1003 | N |  |  | N |  |  | Y | 0x8012 | 0x1003
SSU 1–N Address | NA | 0x1814+(N-1)*16 | UINT16 |  | 0 |  | N | N | N | N | N | N | N | N |  | N |  | Y |  | Y | Y | Y | Y | N | Y | N |  |  | N |  |  | Y | 0x8012 | 0x1001 | Y | 0x8012 | 0x1001 | N |  |  | N |  |  | Y | 0x8012 | 0x1001 | Y | 0x8012 | 0x1001 | Y | 0x8012 | 0x1001 | N |  |  | N |  |  | Y | 0x8012 | 0x1001 | Y | 0x8012 | 0x1001 | N |  |  | N |  |  | Y | 0x8012 | 0x1001 | N |  |  | N |  |  | Y | 0x8012 | 0x1001
SSU 1–N Output Power | kW | 0x1815~0x1816+(N-1)*16 | UINT32 |  | 2 |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers Reserved(0x1BC7~0x1BCF)for other SSU | [23 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Number Of Battery Test Records(N) | NA | 0x1BD0 | UINT16 | 2 | 0 | The max value is 10. | N | N | N | N | Y | Y | N | N |  | N |  | Y |  | Y | Y | N | Y | N | Y | N |  |  | N |  |  | Y | According to Battery Test Report |  | Y | According to Battery Test Report |  | N |  |  | N |  |  | Y | According to Battery Test Report |  | Y | According to Battery Test Report |  | N |  |  | N |  |  | N |  |  | Y | According to Battery Test Report |  | Y | According to Battery Test Report |  | N |  |  | N |  |  | Y | According to Battery Test Report |  | N |  |  | N |  |  | Y | According to Battery Test Report
Battery Test Start Time (Year) | NA | 0x1BD1+(N-1)*29 | UINT16 | 2 | 0 |  | N | N | N | N | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | Y
Battery Test Start Time (Month) | NA | 0x1BD2+(N-1)*29 | UINT16 | 2 | 0 |  | N | N | N | N | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | Y
Battery Test Start Time (Day) | NA | 0x1BD3+(N-1)*29 | UINT16 | 2 | 0 |  | N | N | N | N | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | Y
Battery Test Start Time (Hour) | NA | 0x1BD4+(N-1)*29 | UINT16 | 2 | 0 |  | N | N | N | N | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | Y
Battery Test Start Time (Minute) | NA | 0x1BD5+(N-1)*29 | UINT16 | 2 | 0 |  | N | N | N | N | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | Y
Battery Test Start Time (Second) | NA | 0x1BD6+(N-1)*29 | UINT16 | 2 | 0 |  | N | N | N | N | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | Y
Battery Test End Time (Year) | NA | 0x1BD7+(N-1)*29 | UINT16 | 2 | 0 |  | N | N | N | N | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | Y
Battery Test End Time (Month) | NA | 0x1BD8+(N-1)*29 | UINT16 | 2 | 0 |  | N | N | N | N | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | Y
Battery Test End Time (Day) | NA | 0x1BD9+(N-1)*29 | UINT16 | 2 | 0 |  | N | N | N | N | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | Y
Battery Test End Time (Hour) | NA | 0x1BDA+(N-1)*29 | UINT16 | 2 | 0 |  | N | N | N | N | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | Y
Battery Test End Time (Minute) | NA | 0x1BDB+(N-1)*29 | UINT16 | 2 | 0 |  | N | N | N | N | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | Y
Battery Test End Time (Second) | NA | 0x1BDC+(N-1)*29 | UINT16 | 2 | 0 |  | N | N | N | N | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | Y
Battery Test Type | NA | 0x1BDD+(N-1)*29 | UINT16 | 2 | 0 | [0=No test]/ [1=Manual test]/ [2=AC fail test]/ [3=Scheduled test]/ [4=Short test]/ [5=Simplified test] | N | N | N | N | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | Y
Battery Test Stop Reason | NA | 0x1BDE+(N-1)*29 | UINT16 | 2 | 0 | [0=No cause]/ [1=Low voltage]/ [2=Exceeded time limit]/ [3=Mains recovery]/ [4=Stop test manually]/ [5=Fault alarm]/ [6=Low capacity]/ [7=Low temperature] | N | N | N | N | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | Y
Battery Test Start Voltage | V | 0x1BDF+(N-1)*29 | UINT32 | 4 | 1 |  | N | N | N | N | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | Y
Battery Test End Voltage | V | 0x1BE1+(N-1)*29 | UINT32 | 4 | 1 |  | N | N | N | N | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | Y
Battery Test Average Discharge Current | A | 0x1BE3+(N-1)*29 | INT32 | 4 | 1 |  | N | N | N | N | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | Y
Battery Test Discharge Capacity | Ah | 0x1BE5+(N-1)*29 | UINT32 | 4 | 1 |  | N | N | N | N | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | Y
Battery Test End Battery Temperature | ℃ | 0x1BE7+(N-1)*29 | INT32 | 4 | 0 |  | N | N | N | N | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | Y
Battery Test Result | NA | 0x1BE9+(N-1)*29 | UINT16 | 2 | 0 | [0=Abnormal end]/ [1=Test normal]/ [2=Battery pre-alarm]/ [3=Battery alm] | N | N | N | N | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | Y
|  | Registers Reserved(0x1BEA~0x1BED+(N-1)*29)) |  |  |  |  | N | N | N | N | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
|  | Registers Reserved(0x1CF3~0x1CFF) | [23 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Number of rectifier cabinets | NA | 0x9000 | UINT16 | 2 | 0 | 8 in maximum | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8232 | 0x1639 | N |  |  | N |  |  | N |  |  | Y | 0x8232 | 0x1639 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8232 | 0x1639 | Y | 0x8232 | 0x1639 | N |  |  | N |  |  | Y | 0x8232 | 0x1639 | N |  |  | N |  |  | Y | 0x8232 | 0x1639
Number of modules in rectifier cabinet N# N: 1–8 | NA | 0x9001+(N-1) | UINT16 | 2 | 0 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9004 | 0x1500 | N |  |  | N |  |  | N |  |  | Y | 0x9004 | 0x1500 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9004 | 0x1500 | Y | 0x9004 | 0x1500 | N |  |  | N |  |  | Y | 0x9004 | 0x1500 | N |  |  | N |  |  | Y | 0x9004 | 0x1500
|  | Registers 0x9009–0x901F reserved | [23 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Number of DC cabinets | NA | 0x9020 | UINT16 | 2 | 0 | 14 in maximum | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8232 | 0x1637 | N |  |  | N |  |  | N |  |  | Y | 0x8232 | 0x1637 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8232 | 0x1637 | Y | 0x8232 | 0x1637 | N |  |  | N |  |  | Y | 0x8232 | 0x1637 | N |  |  | N |  |  | Y | 0x8232 | 0x1637
Number of PDUs in DC cabinet N# N: 1–14 | NA | 0x9021+(N-1)*9 | UINT16 | 2 | 0 | 3 in maximum | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x19C9 | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x19C9 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x19C9 | Y | 0x826A | 0x19C9 | N |  |  | N |  |  | Y | 0x826A | 0x19C9 | N |  |  | N |  |  | Y | 0x826A | 0x19C9
Number of load current routes for PDU 1 in DC cabinet N# N:1–14 | NA | 0x9022+(N-1)*9 | UINT16 | 2 | 0 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x2014 | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x2014 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x2014 | Y | 0x826A | 0x2014 | N |  |  | N |  |  | Y | 0x826A | 0x2014 | N |  |  | N |  |  | Y | 0x826A | 0x2014
Number of load fuses for PDU 1 in DC cabinet N# N:1–14 | NA | 0x9023+(N-1)*9 | UINT16 | 2 | 0 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x2015 | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x2015 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x2015 | Y | 0x826A | 0x2015 | N |  |  | N |  |  | Y | 0x826A | 0x2015 | N |  |  | N |  |  | Y | 0x826A | 0x2015
Number of load current routes for PDU 2 in DC cabinet N# N:1–14 | NA | 0x9024+(N-1)*9 | UINT16 | 2 | 0 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x2115 | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x2115 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x2115 | Y | 0x826A | 0x2115 | N |  |  | N |  |  | Y | 0x826A | 0x2115 | N |  |  | N |  |  | Y | 0x826A | 0x2115
Number of load fuses for PDU 2 in DC cabinet N# N:1–14 | NA | 0x9025+(N-1)*9 | UINT16 | 2 | 0 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x2116 | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x2116 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x2116 | Y | 0x826A | 0x2116 | N |  |  | N |  |  | Y | 0x826A | 0x2116 | N |  |  | N |  |  | Y | 0x826A | 0x2116
Number of load current routes for PDU 3 in DC cabinet N# N: 1–14 | NA | 0x9026+(N-1)*9 | UINT16 | 2 | 0 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x2214 | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x2214 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x2214 | Y | 0x826A | 0x2214 | N |  |  | N |  |  | Y | 0x826A | 0x2214 | N |  |  | N |  |  | Y | 0x826A | 0x2214
Number of load fuses for PDU 3 in DC cabinet N# N: 1–14 | NA | 0x9027+(N-1)*9 | UINT16 | 2 | 0 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x2215 | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x2215 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x2215 | Y | 0x826A | 0x2215 | N |  |  | N |  |  | Y | 0x826A | 0x2215 | N |  |  | N |  |  | Y | 0x826A | 0x2215
Number of battery current routes in DC cabinet N# N: 1–14 | NA | 0x9028+(N-1)*9 | UINT16 | 2 | 0 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x2003 | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x2003 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x2003 | Y | 0x826A | 0x2003 | N |  |  | N |  |  | Y | 0x826A | 0x2003 | N |  |  | N |  |  | Y | 0x826A | 0x2003
Number of battery fuses in DC cabinet N# N: 1–14 | NA | 0x9029+(N-1)*9 | UINT16 | 2 | 0 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x2010 | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x2010 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x2010 | Y | 0x826A | 0x2010 | N |  |  | N |  |  | Y | 0x826A | 0x2010 | N |  |  | N |  |  | Y | 0x826A | 0x2010
|  | Register 0x909F reserved |  | 2 | [21 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Number of combined cabinets | NA | 0x90A0 | UINT16 | 2 | 0 | 8 in maximum | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8232 | 0x116B | N |  |  | N |  |  | N |  |  | Y | 0x8232 | 0x116B | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8232 | 0x116B | Y | 0x8232 | 0x116B | N |  |  | N |  |  | Y | 0x8232 | 0x116B | N |  |  | N |  |  | Y | 0x8232 | 0x116B
Number of modules in combined cabinet N# N: 1–8 | NA | 0x90A1+(N-1)*8 | UINT16 | 2 | 0 | 60 in maximum | Y | N | N | N | N | Y | Y | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9003 | 0x1500 | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x1500 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x1500 | Y | 0x9003 | 0x1500 | N |  |  | N |  |  | Y | 0x9003 | 0x1500 | N |  |  | N |  |  | Y | 0x9003 | 0x1500
Number of load current routes in combined cabinet N# N: 1–8 | NA | 0x90A2+(N-1)*8 | UINT16 | 2 | 0 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9003 | 0x2014 | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x2014 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x2014 | Y | 0x9003 | 0x2014 | N |  |  | N |  |  | Y | 0x9003 | 0x2014 | N |  |  | N |  |  | Y | 0x9003 | 0x2014
Number of load fuses in combined cabinet N# N: 1–8 | NA | 0x90A3+(N-1)*8 | UINT16 | 2 | 0 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9003 | 0x2015 | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x2015 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x2015 | Y | 0x9003 | 0x2015 | N |  |  | N |  |  | Y | 0x9003 | 0x2015 | N |  |  | N |  |  | Y | 0x9003 | 0x2015
Number of battery current routes in combined cabinet N# N: 1–8 | NA | 0x90A4+(N-1)*8 | UINT16 | 2 | 0 |  | Y | N | N | N | N | Y | Y | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9003 | 0x2003 | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x2003 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x2003 | Y | 0x9003 | 0x2003 | N |  |  | N |  |  | Y | 0x9003 | 0x2003 | N |  |  | N |  |  | Y | 0x9003 | 0x2003
Number of battery fuses in combined cabinet N# N: 1–8 | NA | 0x90A5+(N-1)*8 | UINT16 | 2 | 0 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9003 | 0x2010 | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x2010 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x2010 | Y | 0x9003 | 0x2010 | N |  |  | N |  |  | Y | 0x9003 | 0x2010 | N |  |  | N |  |  | Y | 0x9003 | 0x2010
|  | Reserve three registers for each cabinet. |  |  |  |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
|  | Registers 0x90E1–0x90EF reserved | [11 empty] | N | [11 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Number of AC PDCs | NA | 0x9100 | UINT16 | 2 | 0 | 8 in maximum | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8232 | 0x1636 | N |  |  | N |  |  | N |  |  | Y | 0x8232 | 0x1636 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8232 | 0x1636 | Y | 0x8232 | 0x1636 | N |  |  | N |  |  | Y | 0x8232 | 0x1636 | N |  |  | N |  |  | Y | 0x8232 | 0x1636
Number of AC current routes in AC PDC N# N:1–8 | NA | 0x9101+(N-1) | UINT16 | 2 | 0 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8269 | 0x1056 | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1056 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1056 | Y | 0x8269 | 0x1056 | N |  |  | N |  |  | Y | 0x8269 | 0x1056 | N |  |  | N |  |  | Y | 0x8269 | 0x1056
|  | Registers 0x9108–0x912F reserved | [11 empty] | N | [11 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Current of load branch M in combined cabinet N# N: 1–8; M: 1–30 | A | 0x9130+(N-1)*70+(M-1) | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9003 | 0x1101~0x111E | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x1101~0x111E | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x1101~0x111E | Y | 0x9003 | 0x1101~0x111E | N |  |  | N |  |  | Y | 0x9003 | 0x1101~0x111E | N |  |  | N |  |  | Y | 0x9003 | 0x1101~0x111E
Power of load branch M in combined cabinet N# N: 1–8; M: 1–30 | kW | 0x9130+(N-1)*70+(M-1)+30 | UINT16 | 2 | 2 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9003 | 0x111F~0x113C | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x111F~0x113C | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x111F~0x113C | Y | 0x9003 | 0x111F~0x113C | N |  |  | N |  |  | Y | 0x9003 | 0x111F~0x113C | N |  |  | N |  |  | Y | 0x9003 | 0x111F~0x113C
Current of battery branch M in combined cabinet N# N: 1–8; M: 1–10 | A | 0x9130+(N-1)*70+(M-1)+30+30 | INT16 | 2 | 1 |  | Y | N | N | N | N | Y | Y | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9003 | 0x1010~0x1019 | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x1010~0x1019 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x1010~0x1019 | Y | 0x9003 | 0x1010~0x1019 | N |  |  | N |  |  | Y | 0x9003 | 0x1010~0x1019 | N |  |  | N |  |  | Y | 0x9003 | 0x1010~0x1019
Bus Bar Voltage in combined cabinet N# N: 1–8; | V | 0x9360+(N-1)*8 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Total Load Current in combined cabinet N# N: 1–8; | A | 0x9361+(N-1)*8 | INT16 | 2 | 1 |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Ambient Temperature in combined cabinet N# N: 1–8; | degC | 0x9362+(N-1)*8 | INT16 | 2 | 0 |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Ambient Humidity in combined cabinet N# N: 1–8; | % | 0x9363+(N-1)*8 | UINT16 | 2 | 0 |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Battery Temperature in combined cabinet N# N: 1–8; | degC | 0x9364+(N-1)*8 | INT16 | 2 | 0 |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Battery SOC in combined cabinet N# N: 1–8; | % | 0x9365+(N-1)*8 | UINT16 | 2 | 0 |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AC Energy Consumption in combined cabinet N# N: 1–8; | KWh | 0x9366+(N-1)*8 | UINT32 | 4 | 1 |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers 0x93A0–0x9ABF reserved | [23 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Phase L1 current of AC cabinet N# N: 1–8 | A | 0x9AC0+(N-1)*12 |  | 2 | 1 | Reports phase L1 current if the system is single-phase. | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8269 | 0x1017 | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1017 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1017 | Y | 0x8269 | 0x1017 | N |  |  | N |  |  | Y | 0x8269 | 0x1017 | N |  |  | N |  |  | Y | 0x8269 | 0x1017
Phase L2 current of AC cabinet N# N: 1–8 | A | 0x9AC1+(N-1)*12 | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8269 | 0x1018 | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1018 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1018 | Y | 0x8269 | 0x1018 | N |  |  | N |  |  | Y | 0x8269 | 0x1018 | N |  |  | N |  |  | Y | 0x8269 | 0x1018
Phase L3 current of AC cabinet N# N: 1–8 | A | 0x9AC2+(N-1)*12 | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8269 | 0x1019 | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1019 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1019 | Y | 0x8269 | 0x1019 | N |  |  | N |  |  | Y | 0x8269 | 0x1019 | N |  |  | N |  |  | Y | 0x8269 | 0x1019
AC L1/L1L2 voltage for the first route in AC cabinet N# N: 1–8 | V | 0x9AC3+(N-1)*12 | UINT16 | 2 | 1 | Reports phase L1 current if the system is single-phase. | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8269 | 0x1063 | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1063 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1063 | Y | 0x8269 | 0x1063 | N |  |  | N |  |  | Y | 0x8269 | 0x1063 | N |  |  | N |  |  | Y | 0x8269 | 0x1063
AC L2/L2L3 voltage for the first route in AC cabinet N# N: 1–8 | V | 0x9AC4+(N-1)*12 | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8269 | 0x1064 | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1064 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1064 | Y | 0x8269 | 0x1064 | N |  |  | N |  |  | Y | 0x8269 | 0x1064 | N |  |  | N |  |  | Y | 0x8269 | 0x1064
AC L3/L3L1 voltage for the first route in AC cabinet N# N: 1–8 | V | 0x9AC5+(N-1)*12 | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8269 | 0x1065 | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1065 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1065 | Y | 0x8269 | 0x1065 | N |  |  | N |  |  | Y | 0x8269 | 0x1065 | N |  |  | N |  |  | Y | 0x8269 | 0x1065
AC frequency of the first route in AC cabinet N# N: 1–8 | Hz | 0x9AC6+(N-1)*12 | UINT16 | 2 | 0 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8269 | 0x100D | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x100D | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x100D | Y | 0x8269 | 0x100D | N |  |  | N |  |  | Y | 0x8269 | 0x100D | N |  |  | N |  |  | Y | 0x8269 | 0x100D
AC L1/L1L2 voltage for the second route in AC cabinet N# N: 1–8 | V | 0x9AC7+(N-1)*12 | UINT16 | 2 | 1 | Reports phase L1 voltage if the system is single-phase. | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8269 | 0x1066 | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1066 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1066 | Y | 0x8269 | 0x1066 | N |  |  | N |  |  | Y | 0x8269 | 0x1066 | N |  |  | N |  |  | Y | 0x8269 | 0x1066
AC L2/L2L3 voltage for the second route in AC cabinet N# N: 1–8 | V | 0x9AC8+(N-1)*12 | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8269 | 0x1067 | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1067 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1067 | Y | 0x8269 | 0x1067 | N |  |  | N |  |  | Y | 0x8269 | 0x1067 | N |  |  | N |  |  | Y | 0x8269 | 0x1067
AC L3/L3L1 voltage for the second route in AC cabinet N# N: 1–8 | V | 0x9AC9+(N-1)*12 | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8269 | 0x1068 | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1068 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1068 | Y | 0x8269 | 0x1068 | N |  |  | N |  |  | Y | 0x8269 | 0x1068 | N |  |  | N |  |  | Y | 0x8269 | 0x1068
AC frequency of the second route in AC cabinet N# N: 1–8 | Hz | 0x9ACA+(N-1)*12 | UINT16 | 2 | 0 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8269 | 0x1015 | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1015 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8269 | 0x1015 | Y | 0x8269 | 0x1015 | N |  |  | N |  |  | Y | 0x8269 | 0x1015 | N |  |  | N |  |  | Y | 0x8269 | 0x1015
|  | Reserve one register for each cabinet. |  |  |  |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N | [5 empty] | N | [5 empty] | N | [5 empty] | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
|  | Registers 0x9B20–0x9BFF reserved | [23 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Phase L1 current of combined cabinet N# N: 1–8 | A | 0x9C00+(N-1)*8 | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | Y | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x14AC | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AC | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AC | Y | 0x8231 | 0x14AC | N |  |  | N |  |  | Y | 0x8231 | 0x14AC | N |  |  | N |  |  | Y | 0x8231 | 0x14AC
Phase L2 current of combined cabinet N# N: 1–8 | A | 0x9C01+(N-1)*8 | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | Y | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x14AD | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AD | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AD | Y | 0x8231 | 0x14AD | N |  |  | N |  |  | Y | 0x8231 | 0x14AD | N |  |  | N |  |  | Y | 0x8231 | 0x14AD
Phase L3 current of combined cabinet N# N: 1–8 | A | 0x9C02+(N-1)*8 | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | Y | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x14AE | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AE | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AE | Y | 0x8231 | 0x14AE | N |  |  | N |  |  | Y | 0x8231 | 0x14AE | N |  |  | N |  |  | Y | 0x8231 | 0x14AE
L1/L1L2 voltage for combined cabinet N# N: 1–8 | V | 0x9C03+(N-1)*8 | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | Y | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x14A9 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14A9 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14A9 | Y | 0x8231 | 0x14A9 | N |  |  | N |  |  | Y | 0x8231 | 0x14A9 | N |  |  | N |  |  | Y | 0x8231 | 0x14A9
L2/L2L3 voltage for combined cabinet N# N: 1–8 | V | 0x9C04+(N-1)*8 | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | Y | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x14AA | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AA | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AA | Y | 0x8231 | 0x14AA | N |  |  | N |  |  | Y | 0x8231 | 0x14AA | N |  |  | N |  |  | Y | 0x8231 | 0x14AA
L3/L3L1 voltage for combined cabinet N# N: 1–8 | V | 0x9C05+(N-1)*8 | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | Y | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x14AB | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AB | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AB | Y | 0x8231 | 0x14AB | N |  |  | N |  |  | Y | 0x8231 | 0x14AB | N |  |  | N |  |  | Y | 0x8231 | 0x14AB
AC frequency of combined cabinet N# N: 1–8 | Hz | 0x9C06+(N-1)*8 | UINT16 | 2 | 0 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x1822 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1822 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1822 | Y | 0x8231 | 0x1822 | N |  |  | N |  |  | Y | 0x8231 | 0x1822 | N |  |  | N |  |  | Y | 0x8231 | 0x1822
|  | Reserve one register for each cabinet. |  |  |  |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers 0x9C40–0x9C4F reserved | [11 empty] | N |  | N | [9 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Phase L1 current of rectifier cabinet N# N: 1–8 | A | 0x9C50+(N-1)*8 | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x14AC | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AC | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AC | Y | 0x8231 | 0x14AC | N |  |  | N |  |  | Y | 0x8231 | 0x14AC | N |  |  | N |  |  | Y | 0x8231 | 0x14AC
Phase L2 current of rectifier cabinet N# N: 1–8 | A | 0x9C51+(N-1)*8 | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x14AD | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AD | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AD | Y | 0x8231 | 0x14AD | N |  |  | N |  |  | Y | 0x8231 | 0x14AD | N |  |  | N |  |  | Y | 0x8231 | 0x14AD
Phase L3 current of rectifier cabinet N# N: 1–8 | A | 0x9C52+(N-1)*8 | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x14AE | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AE | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AE | Y | 0x8231 | 0x14AE | N |  |  | N |  |  | Y | 0x8231 | 0x14AE | N |  |  | N |  |  | Y | 0x8231 | 0x14AE
L1/L1L2 voltage for rectifier cabinet N# N: 1–8 | V | 0x9C53+(N-1)*8 | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x14A9 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14A9 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14A9 | Y | 0x8231 | 0x14A9 | N |  |  | N |  |  | Y | 0x8231 | 0x14A9 | N |  |  | N |  |  | Y | 0x8231 | 0x14A9
L2/L2L3 voltage for rectifier cabinet N# N: 1–8 | V | 0x9C54+(N-1)*8 | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x14AA | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AA | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AA | Y | 0x8231 | 0x14AA | N |  |  | N |  |  | Y | 0x8231 | 0x14AA | N |  |  | N |  |  | Y | 0x8231 | 0x14AA
L3/L3L1 voltage for rectifier cabinet N# N: 1–8 | V | 0x9C55+(N-1)*8 | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x14AB | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AB | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x14AB | Y | 0x8231 | 0x14AB | N |  |  | N |  |  | Y | 0x8231 | 0x14AB | N |  |  | N |  |  | Y | 0x8231 | 0x14AB
AC frequency of rectifier cabinet N# N: 1–8 | Hz | 0x9C56+(N-1)*8 | UINT16 | 2 | 0 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x1822 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1822 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1822 | Y | 0x8231 | 0x1822 | N |  |  | N |  |  | Y | 0x8231 | 0x1822 | N |  |  | N |  |  | Y | 0x8231 | 0x1822
|  | Reserve one register for each cabinet. |  |  |  |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers 0x9C90–0x9C9F reserved | [11 empty] | N | [11 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Current of load branch M for PDU 1 in DC cabinet N# N: 1–14; M: 1–30 | A | 0x9CA0+(N-1)*190+(M-1) | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x1101~0x111E | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x1101~0x111E | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x1101~0x111E | Y | 0x826A | 0x1101~0x111E | N |  |  | N |  |  | Y | 0x826A | 0x1101~0x111E | N |  |  | N |  |  | Y | 0x826A | 0x1101~0x111E
Power of load branch M for PDU 1 in DC cabinet N# N: 1–14; M: 1–30 | kW | 0x9CA0+(N-1)*190+(M-1)+30 | UINT16 | 2 | 2 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x111F~0x113C | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x111F~0x113C | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x111F~0x113C | Y | 0x826A | 0x111F~0x113C | N |  |  | N |  |  | Y | 0x826A | 0x111F~0x113C | N |  |  | N |  |  | Y | 0x826A | 0x111F~0x113C
Current of load branch M for PDU 2 in DC cabinet N# N: 1–14; M: 1–30 | A | 0x9CA0+(N-1)*190+(M-1)+30+30 | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x1401~0x141E | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x1401~0x141E | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x1401~0x141E | Y | 0x826A | 0x1401~0x141E | N |  |  | N |  |  | Y | 0x826A | 0x1401~0x141E | N |  |  | N |  |  | Y | 0x826A | 0x1401~0x141E
Power of load branch M for PDU 2 in DC cabinet N# N: 1–14; M: 1–30 | kW | 0x9CA0+(N-1)*190+(M-1)+30+30+30 | UINT16 | 2 | 2 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x141F~0x143C | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x141F~0x143C | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x141F~0x143C | Y | 0x826A | 0x141F~0x143C | N |  |  | N |  |  | Y | 0x826A | 0x141F~0x143C | N |  |  | N |  |  | Y | 0x826A | 0x141F~0x143C
Current of load branch M for PDU 3 in DC cabinet N# N: 1–14; M: 1–30 | A | 0x9CA0+(N-1)*190+(M-1)+30+30+30+30 | UINT16 | 2 | 1 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x1801~0x181E | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x1801~0x181E | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x1801~0x181E | Y | 0x826A | 0x1801~0x181E | N |  |  | N |  |  | Y | 0x826A | 0x1801~0x181E | N |  |  | N |  |  | Y | 0x826A | 0x1801~0x181E
Power of load branch M for PDU 3 in DC cabinet N# N: 1–14; M: 1–30 | kW | 0x9CA0+(N-1)*190+(M-1)+30+30+30+30+30 | UINT16 | 2 | 2 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x181F~0x183C | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x181F~0x183C | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x181F~0x183C | Y | 0x826A | 0x181F~0x183C | N |  |  | N |  |  | Y | 0x826A | 0x181F~0x183C | N |  |  | N |  |  | Y | 0x826A | 0x181F~0x183C
Current of battery branch M in DC cabinet N# N: 1–14; M: 1–10 | A | 0x9CA0+(N-1)*190+(M-1)+30+30+30+30+30+30 | INT16 | 2 | 1 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x1010~0x1019 | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x1010~0x1019 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x1010~0x1019 | Y | 0x826A | 0x1010~0x1019 | N |  |  | N |  |  | Y | 0x826A | 0x1010~0x1019 | N |  |  | N |  |  | Y | 0x826A | 0x1010~0x1019
|  | Registers 0xA704–0xA70F reserved | [23 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
57V Side Port Voltage in Power Unit N# N: 1–3 | V | 0xA710+(N-1)*2 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
57V Side Load Current in Power Unit N# N: 1–3 | V | 0xA711+(N-1)*2 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
[26 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Number of ACB Cabinets | NA | 0xA720 | UINT16 | 2 | 0 | 16 in maximum, for DPS, its value always is 1. | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Battery Status | NA | 0xA701 | UINT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | Y | 0x8018 | 0x1001 | N | 0x8018 | 0x1001 | N |  |  | N |  |  | Y | 0x8018 | 0x1001 | N | 0x8018 | 0x1001 | N |  |  | Y | 0x8018 | 0x1001 | N |  |  | Y | 0x8018 | 0x1001 | N | 0x8018 | 0x1001 | N | 0x8018 | 0x1001 | Y | 0x8018 | 0x1001 | N |  |  | N | 0x8018 | 0x1001 | Y | 0x8018 | 0x1001 | N |  |  | N | 0x8018 | 0x1001
Battery Voltage | V | 0xA702~0xA703 | UINT32 | 4 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | Y | 0x8018 | 0x107D | N | 0x8018 | 0x107D | N |  |  | N |  |  | Y | 0x8018 | 0x107D | N | 0x8018 | 0x107D | N |  |  | Y | 0x8018 | 0x107D | N |  |  | Y | 0x8018 | 0x107D | N | 0x8018 | 0x107D | N | 0x8018 | 0x107D | Y | 0x8018 | 0x107D | N |  |  | N | 0x8018 | 0x107D | Y | 0x8018 | 0x107D | N |  |  | N | 0x8018 | 0x107D
Battery Current | A | 0xA704~0xA705 | INT32 | 4 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N |  | N | N |  |  | Y | 0x8018 | 0x107E | N | 0x8018 | 0x107E | N |  |  | N |  |  | Y | 0x8018 | 0x107E | N | 0x8018 | 0x107E | N |  |  | Y | 0x8018 | 0x107E | N |  |  | Y | 0x8018 | 0x107E | N | 0x8018 | 0x107E | N | 0x8018 | 0x107E | Y | 0x8018 | 0x107E | N |  |  | N | 0x8018 | 0x107E | Y | 0x8018 | 0x107E | N |  |  | N | 0x8018 | 0x107E
Battery Temperature | degC | 0xA706 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8018 | 0x1004 | Y | 0x8018 | 0x1004 | N |  |  | N |  |  | Y | 0x8018 | 0x1004 | Y | 0x8018 | 0x1004 | N |  |  | Y | 0x8018 | 0x1004 | N |  |  | Y | 0x8018 | 0x1004 | Y | 0x8018 | 0x1004 | Y | 0x8018 | 0x1004 | Y | 0x8018 | 0x1004 | N |  |  | Y | 0x8018 | 0x1004 | Y | 0x8018 | 0x1004 | N |  |  | Y | 0x8018 | 0x1004
Remaining Battery Capacity Percent | % | 0xA707 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | Y | 0x8018 | 0x1005 | N | 0x8018 | 0x1005 | N |  |  | N |  |  | Y | 0x8018 | 0x1005 | N | 0x8018 | 0x1005 | N |  |  | Y | 0x8018 | 0x1005 | N |  |  | Y | 0x8018 | 0x1005 | N | 0x8018 | 0x1005 | N | 0x8018 | 0x1005 | Y | 0x8018 | 0x1005 | N |  |  | N | 0x8018 | 0x1005 | Y | 0x8018 | 0x1005 | N |  |  | N | 0x8018 | 0x1005
Battery Backup Time | h | 0xA708~0xA709 | UINT32 | 4 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | Y | 0x8018 | 0x1006 | N | 0x8018 | 0x1006 | N |  |  | N |  |  | Y | 0x8018 | 0x1006 | N | 0x8018 | 0x1006 | N |  |  | Y | 0x8018 | 0x1006 | N |  |  | Y | 0x8018 | 0x1006 | N | 0x8018 | 0x1006 | N | 0x8018 | 0x1006 | Y | 0x8018 | 0x1006 | N |  |  | N | 0x8018 | 0x1006 | Y | 0x8018 | 0x1006 | N |  |  | N | 0x8018 | 0x1006
Battery SOH | % | 0xA70A | UINT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | Y | 0x8018 | 0x1007 | N | 0x8018 | 0x1007 | N |  |  | N |  |  | Y | 0x8018 | 0x1007 | N | 0x8018 | 0x1007 | N |  |  | Y | 0x8018 | 0x1007 | N |  |  | Y | 0x8018 | 0x1007 | N | 0x8018 | 0x1007 | N | 0x8018 | 0x1007 | Y | 0x8018 | 0x1007 | N |  |  | N | 0x8018 | 0x1007 | Y | 0x8018 | 0x1007 | N |  |  | N | 0x8018 | 0x1007
Total Discharge Times | NA | 0xA70B | UINT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | Y | 0x8018 | 0x1008 | N | 0x8018 | 0x1008 | N |  |  | N |  |  | Y | 0x8018 | 0x1008 | N | 0x8018 | 0x1008 | N |  |  | Y | 0x8018 | 0x1008 | N |  |  | Y | 0x8018 | 0x1008 | N | 0x8018 | 0x1008 | N | 0x8018 | 0x1008 | Y | 0x8018 | 0x1008 | N |  |  | N | 0x8018 | 0x1008 | Y | 0x8018 | 0x1008 | N |  |  | N | 0x8018 | 0x1008
Total Discharge Capacity | kWh | 0xA70C~0xA70D | UINT32 | 4 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | Y | 0x8018 | 0x1009 | N | 0x8018 | 0x1009 | N |  |  | N |  |  | Y | 0x8018 | 0x1009 | N | 0x8018 | 0x1009 | N |  |  | Y | 0x8018 | 0x1009 | N |  |  | Y | 0x8018 | 0x1009 | N | 0x8018 | 0x1009 | N | 0x8018 | 0x1009 | Y | 0x8018 | 0x1009 | N |  |  | N | 0x8018 | 0x1009 | Y | 0x8018 | 0x1009 | N |  |  | N | 0x8018 | 0x1009
Total Capacity | Ah | 0xA70E~0xA70F | UINT32 | 4 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | Y | 0x8018 | 0x100C | N | 0x8018 | 0x100C | N |  |  | N |  |  | Y | 0x8018 | 0x100C | N | 0x8018 | 0x100C | N |  |  | Y | 0x8018 | 0x100C | N |  |  | Y | 0x8018 | 0x100C | N | 0x8018 | 0x100C | N | 0x8018 | 0x100C | Y | 0x8018 | 0x100C | N |  |  | N | 0x8018 | 0x100C | Y | 0x8018 | 0x100C | N |  |  | N | 0x8018 | 0x100C
Number of Normal Comm. BMUs | NA | 0xA710 | UINT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | Y | 0x8018 | 0x1017 | N | 0x8018 | 0x1017 | N |  |  | N |  |  | Y | 0x8018 | 0x1017 | N | 0x8018 | 0x1017 | N |  |  | Y | 0x8018 | 0x1017 | N |  |  | Y | 0x8018 | 0x1017 | N | 0x8018 | 0x1017 | N | 0x8018 | 0x1017 | Y | 0x8018 | 0x1017 | N |  |  | N | 0x8018 | 0x1017 | Y | 0x8018 | 0x1017 | N |  |  | N | 0x8018 | 0x1017
Battery First On | NA | 0xA711 | UINT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N | 0x8018 | 0x1070 | N |  |  | N |  |  | N |  |  | N | 0x8018 | 0x1070 | N |  |  | N |  |  | N |  |  | N |  |  | N | 0x8018 | 0x1070 | N | 0x8018 | 0x1070 | N |  |  | N |  |  | N | 0x8018 | 0x1070 | N |  |  | N |  |  | N | 0x8018 | 0x1070
Main Back State | NA | 0xA712 | UINT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N | 0x8018 | 0x107C | N |  |  | N |  |  | N |  |  | N | 0x8018 | 0x107C | N |  |  | N |  |  | N |  |  | N |  |  | N | 0x8018 | 0x107C | N | 0x8018 | 0x107C | N |  |  | N |  |  | N | 0x8018 | 0x107C | N |  |  | N |  |  | N | 0x8018 | 0x107C
iLock Enabled | NA | 0xA713 | UINT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | Y | 0x8018 | 0x108E | N | 0x8018 | 0x108E | N |  |  | N |  |  | Y | 0x8018 | 0x108E | N | 0x8018 | 0x108E | N |  |  | N |  |  | N |  |  | Y | 0x8018 | 0x108E | N | 0x8018 | 0x108E | N | 0x8018 | 0x108E | Y | 0x8018 | 0x108E | N |  |  | N | 0x8018 | 0x108E | Y | 0x8018 | 0x108E | N |  |  | N | 0x8018 | 0x108E
Test Status | NA | 0xA714 | UINT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | Y | 0x8018 | 0x1092 | N | 0x8018 | 0x1092 | N |  |  | N |  |  | Y | 0x8018 | 0x1092 | N | 0x8018 | 0x1092 | N |  |  | N |  |  | N |  |  | Y | 0x8018 | 0x1092 | N | 0x8018 | 0x1092 | N | 0x8018 | 0x1092 | Y | 0x8018 | 0x1092 | N |  |  | N | 0x8018 | 0x1092 | Y | 0x8018 | 0x1092 | N |  |  | N | 0x8018 | 0x1092
Charge/Discharge Power | kW | 0xA715~0xA716 | INT32 | 4 | 2 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | Y | 0x8018 | 0x1110 | N | 0x8018 | 0x1110 | N |  |  | N |  |  | Y | 0x8018 | 0x1110 | N | 0x8018 | 0x1110 | N |  |  | Y | 0x8018 | 0x1110 | N |  |  | Y | 0x8018 | 0x1110 | N | 0x8018 | 0x1110 | N | 0x8018 | 0x1110 | Y | 0x8018 | 0x1110 | N |  |  | N | 0x8018 | 0x1110 | Y | 0x8018 | 0x1110 | N |  |  | N | 0x8018 | 0x1110
|  | Registers Reserved For ACB Group (0xA717~0xA730) | [29 empty] | N |  |  | N | [8 empty] | N |  |  | N | [11 empty] | N |  |  | N | [8 empty] | N | [8 empty] | N
Battery Voltage N: 1-32 | V | 0xA731~0xA732+(N-1)*64 | UINT32 | 4 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1006 | Y | 0x8019 | 0x1006 | N |  |  | N |  |  | Y | 0x8019 | 0x1006 | Y | 0x8019 | 0x1006 | N |  |  | Y | 0x8019 | 0x1006 | N |  |  | Y | 0x8019 | 0x1006 | Y | 0x8019 | 0x1006 | Y | 0x8019 | 0x1006 | Y | 0x8019 | 0x1006 | N |  |  | Y | 0x8019 | 0x1006 | Y | 0x8019 | 0x1006 | N |  |  | Y | 0x8019 | 0x1006
Battery Current N: 1-32 | A | 0xA733~0xA734+(N-1)*64 | INT32 | 4 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1007 | Y | 0x8019 | 0x1007 | N |  |  | N |  |  | Y | 0x8019 | 0x1007 | Y | 0x8019 | 0x1007 | N |  |  | Y | 0x8019 | 0x1007 | N |  |  | Y | 0x8019 | 0x1007 | Y | 0x8019 | 0x1007 | Y | 0x8019 | 0x1007 | Y | 0x8019 | 0x1007 | N |  |  | Y | 0x8019 | 0x1007 | Y | 0x8019 | 0x1007 | N |  |  | Y | 0x8019 | 0x1007
Cell Package Voltage N: 1-32 | V | 0xA735~0xA736+(N-1)*64 | UINT32 | 4 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | Y | 0x8019 | 0x1078 | N | 0x8019 | 0x1078 | N |  |  | N |  |  | Y | 0x8019 | 0x1078 | N | 0x8019 | 0x1078 | N |  |  | Y | 0x8019 | 0x1078 | N |  |  | Y | 0x8019 | 0x1078 | N | 0x8019 | 0x1078 | N | 0x8019 | 0x1078 | Y | 0x8019 | 0x1078 | N |  |  | N | 0x8019 | 0x1078 | Y | 0x8019 | 0x1078 | N |  |  | N | 0x8019 | 0x1078
Cell Package Current N: 1-32 | A | 0xA737~0xA738+(N-1)*64 | INT32 | 4 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | Y | 0x8019 | 0x1077 | N | 0x8019 | 0x1077 | N |  |  | N |  |  | Y | 0x8019 | 0x1077 | N | 0x8019 | 0x1077 | N |  |  | Y | 0x8019 | 0x1077 | N |  |  | Y | 0x8019 | 0x1077 | N | 0x8019 | 0x1077 | N | 0x8019 | 0x1077 | Y | 0x8019 | 0x1077 | N |  |  | N | 0x8019 | 0x1077 | Y | 0x8019 | 0x1077 | N |  |  | N | 0x8019 | 0x1077
Battery SOC N: 1-32 | % | 0xA739+(N-1)*64 | UINT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8019 | 0x1008 | Y | 0x8019 | 0x1008 | Y | 0x8019 | 0x1008 | N |  |  | Y | 0x8019 | 0x1008 | Y | 0x8019 | 0x1008 | Y | 0x8019 | 0x1008 | N |  |  | Y | 0x8019 | 0x1008 | Y | 0x8019 | 0x1008 | Y | 0x8019 | 0x1008 | Y | 0x8019 | 0x1008 | Y | 0x8019 | 0x1008 | Y | 0x8019 | 0x1008 | Y | 0x8019 | 0x1008 | Y | 0x8019 | 0x1008 | Y | 0x8019 | 0x1008 | Y | 0x8019 | 0x1008 | Y | 0x8019 | 0x1008
Cell 1 Temperature N: 1-32 | degC | 0xA73A+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1010 | Y | 0x8019 | 0x1010 | N |  |  | N |  |  | Y | 0x8019 | 0x1010 | Y | 0x8019 | 0x1010 | N |  |  | Y | 0x8019 | 0x1010 | N |  |  | Y | 0x8019 | 0x1010 | Y | 0x8019 | 0x1010 | Y | 0x8019 | 0x1010 | Y | 0x8019 | 0x1010 | N |  |  | Y | 0x8019 | 0x1010 | Y | 0x8019 | 0x1010 | N |  |  | Y | 0x8019 | 0x1010
Cell 2 Temperature N: 1-32 | degC | 0xA73B+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1011 | Y | 0x8019 | 0x1011 | N |  |  | N |  |  | Y | 0x8019 | 0x1011 | Y | 0x8019 | 0x1011 | N |  |  | Y | 0x8019 | 0x1011 | N |  |  | Y | 0x8019 | 0x1011 | Y | 0x8019 | 0x1011 | Y | 0x8019 | 0x1011 | Y | 0x8019 | 0x1011 | N |  |  | Y | 0x8019 | 0x1011 | Y | 0x8019 | 0x1011 | N |  |  | Y | 0x8019 | 0x1011
Cell 3 Temperature N: 1-32 | degC | 0xA73C+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1012 | Y | 0x8019 | 0x1012 | N |  |  | N |  |  | Y | 0x8019 | 0x1012 | Y | 0x8019 | 0x1012 | N |  |  | Y | 0x8019 | 0x1012 | N |  |  | Y | 0x8019 | 0x1012 | Y | 0x8019 | 0x1012 | Y | 0x8019 | 0x1012 | Y | 0x8019 | 0x1012 | N |  |  | Y | 0x8019 | 0x1012 | Y | 0x8019 | 0x1012 | N |  |  | Y | 0x8019 | 0x1012
Cell 4 Temperature N: 1-32 | degC | 0xA73D+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1013 | Y | 0x8019 | 0x1013 | N |  |  | N |  |  | Y | 0x8019 | 0x1013 | Y | 0x8019 | 0x1013 | N |  |  | Y | 0x8019 | 0x1013 | N |  |  | Y | 0x8019 | 0x1013 | Y | 0x8019 | 0x1013 | Y | 0x8019 | 0x1013 | Y | 0x8019 | 0x1013 | N |  |  | Y | 0x8019 | 0x1013 | Y | 0x8019 | 0x1013 | N |  |  | Y | 0x8019 | 0x1013
Cell 5 Temperature N: 1-32 | degC | 0xA73E+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1014 | Y | 0x8019 | 0x1014 | N |  |  | N |  |  | Y | 0x8019 | 0x1014 | Y | 0x8019 | 0x1014 | N |  |  | Y | 0x8019 | 0x1014 | N |  |  | Y | 0x8019 | 0x1014 | Y | 0x8019 | 0x1014 | Y | 0x8019 | 0x1014 | Y | 0x8019 | 0x1014 | N |  |  | Y | 0x8019 | 0x1014 | Y | 0x8019 | 0x1014 | N |  |  | Y | 0x8019 | 0x1014
Cell 6 Temperature N: 1-32 | degC | 0xA73F+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1015 | Y | 0x8019 | 0x1015 | N |  |  | N |  |  | Y | 0x8019 | 0x1015 | Y | 0x8019 | 0x1015 | N |  |  | Y | 0x8019 | 0x1015 | N |  |  | Y | 0x8019 | 0x1015 | Y | 0x8019 | 0x1015 | Y | 0x8019 | 0x1015 | Y | 0x8019 | 0x1015 | N |  |  | Y | 0x8019 | 0x1015 | Y | 0x8019 | 0x1015 | N |  |  | Y | 0x8019 | 0x1015
Cell 7 Temperature N: 1-32 | degC | 0xA740+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1016 | Y | 0x8019 | 0x1016 | N |  |  | N |  |  | Y | 0x8019 | 0x1016 | Y | 0x8019 | 0x1016 | N |  |  | Y | 0x8019 | 0x1016 | N |  |  | Y | 0x8019 | 0x1016 | Y | 0x8019 | 0x1016 | Y | 0x8019 | 0x1016 | Y | 0x8019 | 0x1016 | N |  |  | Y | 0x8019 | 0x1016 | Y | 0x8019 | 0x1016 | N |  |  | Y | 0x8019 | 0x1016
Cell 8 Temperature N: 1-32 | degC | 0xA741+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1017 | Y | 0x8019 | 0x1017 | N |  |  | N |  |  | Y | 0x8019 | 0x1017 | Y | 0x8019 | 0x1017 | N |  |  | Y | 0x8019 | 0x1017 | N |  |  | Y | 0x8019 | 0x1017 | Y | 0x8019 | 0x1017 | Y | 0x8019 | 0x1017 | Y | 0x8019 | 0x1017 | N |  |  | Y | 0x8019 | 0x1017 | Y | 0x8019 | 0x1017 | N |  |  | Y | 0x8019 | 0x1017
Cell 9 Temperature N: 1-32 | degC | 0xA742+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1018 | Y | 0x8019 | 0x1018 | N |  |  | N |  |  | Y | 0x8019 | 0x1018 | Y | 0x8019 | 0x1018 | N |  |  | Y | 0x8019 | 0x1018 | N |  |  | Y | 0x8019 | 0x1018 | Y | 0x8019 | 0x1018 | Y | 0x8019 | 0x1018 | Y | 0x8019 | 0x1018 | N |  |  | Y | 0x8019 | 0x1018 | Y | 0x8019 | 0x1018 | N |  |  | Y | 0x8019 | 0x1018
Cell 10 Temperature N: 1-32 | degC | 0xA743+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1019 | Y | 0x8019 | 0x1019 | N |  |  | N |  |  | Y | 0x8019 | 0x1019 | Y | 0x8019 | 0x1019 | N |  |  | Y | 0x8019 | 0x1019 | N |  |  | Y | 0x8019 | 0x1019 | Y | 0x8019 | 0x1019 | Y | 0x8019 | 0x1019 | Y | 0x8019 | 0x1019 | N |  |  | Y | 0x8019 | 0x1019 | Y | 0x8019 | 0x1019 | N |  |  | Y | 0x8019 | 0x1019
Cell 11 Temperature N: 1-32 | degC | 0xA744+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x101A | Y | 0x8019 | 0x101A | N |  |  | N |  |  | Y | 0x8019 | 0x101A | Y | 0x8019 | 0x101A | N |  |  | Y | 0x8019 | 0x101A | N |  |  | Y | 0x8019 | 0x101A | Y | 0x8019 | 0x101A | Y | 0x8019 | 0x101A | Y | 0x8019 | 0x101A | N |  |  | Y | 0x8019 | 0x101A | Y | 0x8019 | 0x101A | N |  |  | Y | 0x8019 | 0x101A
Cell 12 Temperature N: 1-32 | degC | 0xA745+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x101B | Y | 0x8019 | 0x101B | N |  |  | N |  |  | Y | 0x8019 | 0x101B | Y | 0x8019 | 0x101B | N |  |  | Y | 0x8019 | 0x101B | N |  |  | Y | 0x8019 | 0x101B | Y | 0x8019 | 0x101B | Y | 0x8019 | 0x101B | Y | 0x8019 | 0x101B | N |  |  | Y | 0x8019 | 0x101B | Y | 0x8019 | 0x101B | N |  |  | Y | 0x8019 | 0x101B
Cell 13 Temperature N: 1-32 | degC | 0xA746+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x101C | Y | 0x8019 | 0x101C | N |  |  | N |  |  | Y | 0x8019 | 0x101C | Y | 0x8019 | 0x101C | N |  |  | Y | 0x8019 | 0x101C | N |  |  | Y | 0x8019 | 0x101C | Y | 0x8019 | 0x101C | Y | 0x8019 | 0x101C | Y | 0x8019 | 0x101C | N |  |  | Y | 0x8019 | 0x101C | Y | 0x8019 | 0x101C | N |  |  | Y | 0x8019 | 0x101C
Cell 14 Temperature N: 1-32 | degC | 0xA747+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x101D | Y | 0x8019 | 0x101D | N |  |  | N |  |  | Y | 0x8019 | 0x101D | Y | 0x8019 | 0x101D | N |  |  | Y | 0x8019 | 0x101D | N |  |  | Y | 0x8019 | 0x101D | Y | 0x8019 | 0x101D | Y | 0x8019 | 0x101D | Y | 0x8019 | 0x101D | N |  |  | Y | 0x8019 | 0x101D | Y | 0x8019 | 0x101D | N |  |  | Y | 0x8019 | 0x101D
Cell 15 Temperature N: 1-32 | degC | 0xA748+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x101E | Y | 0x8019 | 0x101E | N |  |  | N |  |  | Y | 0x8019 | 0x101E | Y | 0x8019 | 0x101E | N |  |  | Y | 0x8019 | 0x101E | N |  |  | Y | 0x8019 | 0x101E | Y | 0x8019 | 0x101E | Y | 0x8019 | 0x101E | Y | 0x8019 | 0x101E | N |  |  | Y | 0x8019 | 0x101E | Y | 0x8019 | 0x101E | N |  |  | Y | 0x8019 | 0x101E
Cell 16 Temperature N: 1-32 | degC | 0xA749+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x101F | Y | 0x8019 | 0x101F | N |  |  | N |  |  | Y | 0x8019 | 0x101F | Y | 0x8019 | 0x101F | N |  |  | Y | 0x8019 | 0x101F | N |  |  | Y | 0x8019 | 0x101F | Y | 0x8019 | 0x101F | Y | 0x8019 | 0x101F | Y | 0x8019 | 0x101F | N |  |  | Y | 0x8019 | 0x101F | Y | 0x8019 | 0x101F | N |  |  | Y | 0x8019 | 0x101F
Cell 17 Temperature N: 1-32 | degC | 0xA74A+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x10A6 | Y | 0x8019 | 0x10A6 | N |  |  | N |  |  | Y | 0x8019 | 0x10A6 | Y | 0x8019 | 0x10A6 | N |  |  | Y | 0x8019 | 0x10A6 | N |  |  | Y | 0x8019 | 0x10A6 | Y | 0x8019 | 0x10A6 | Y | 0x8019 | 0x10A6 | Y | 0x8019 | 0x10A6 | N |  |  | Y | 0x8019 | 0x10A6 | Y | 0x8019 | 0x10A6 | N |  |  | Y | 0x8019 | 0x10A6
Cell 18 Temperature N: 1-32 | degC | 0xA74B+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x10A7 | Y | 0x8019 | 0x10A7 | N |  |  | N |  |  | Y | 0x8019 | 0x10A7 | Y | 0x8019 | 0x10A7 | N |  |  | Y | 0x8019 | 0x10A7 | N |  |  | Y | 0x8019 | 0x10A7 | Y | 0x8019 | 0x10A7 | Y | 0x8019 | 0x10A7 | Y | 0x8019 | 0x10A7 | N |  |  | Y | 0x8019 | 0x10A7 | Y | 0x8019 | 0x10A7 | N |  |  | Y | 0x8019 | 0x10A7
Cell 19 Temperature N: 1-32 | degC | 0xA74C+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x10A8 | Y | 0x8019 | 0x10A8 | N |  |  | N |  |  | Y | 0x8019 | 0x10A8 | Y | 0x8019 | 0x10A8 | N |  |  | Y | 0x8019 | 0x10A8 | N |  |  | Y | 0x8019 | 0x10A8 | Y | 0x8019 | 0x10A8 | Y | 0x8019 | 0x10A8 | Y | 0x8019 | 0x10A8 | N |  |  | Y | 0x8019 | 0x10A8 | Y | 0x8019 | 0x10A8 | N |  |  | Y | 0x8019 | 0x10A8
Cell 20 Temperature N: 1-32 | degC | 0xA74D+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x10A9 | Y | 0x8019 | 0x10A9 | N |  |  | N |  |  | Y | 0x8019 | 0x10A9 | Y | 0x8019 | 0x10A9 | N |  |  | Y | 0x8019 | 0x10A9 | N |  |  | Y | 0x8019 | 0x10A9 | Y | 0x8019 | 0x10A9 | Y | 0x8019 | 0x10A9 | Y | 0x8019 | 0x10A9 | N |  |  | Y | 0x8019 | 0x10A9 | Y | 0x8019 | 0x10A9 | N |  |  | Y | 0x8019 | 0x10A9
Cell 21 Temperature N: 1-32 | degC | 0xA74E+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x10AA | Y | 0x8019 | 0x10AA | N |  |  | N |  |  | Y | 0x8019 | 0x10AA | Y | 0x8019 | 0x10AA | N |  |  | Y | 0x8019 | 0x10AA | N |  |  | Y | 0x8019 | 0x10AA | Y | 0x8019 | 0x10AA | Y | 0x8019 | 0x10AA | Y | 0x8019 | 0x10AA | N |  |  | Y | 0x8019 | 0x10AA | Y | 0x8019 | 0x10AA | N |  |  | Y | 0x8019 | 0x10AA
Cell 22 Temperature N: 1-32 | degC | 0xA74F+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x10AB | Y | 0x8019 | 0x10AB | N |  |  | N |  |  | Y | 0x8019 | 0x10AB | Y | 0x8019 | 0x10AB | N |  |  | Y | 0x8019 | 0x10AB | N |  |  | Y | 0x8019 | 0x10AB | Y | 0x8019 | 0x10AB | Y | 0x8019 | 0x10AB | Y | 0x8019 | 0x10AB | N |  |  | Y | 0x8019 | 0x10AB | Y | 0x8019 | 0x10AB | N |  |  | Y | 0x8019 | 0x10AB
Cell 1 Voltage N: 1-32 | V | 0xA750+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1020 | Y | 0x8019 | 0x1020 | N |  |  | N |  |  | Y | 0x8019 | 0x1020 | Y | 0x8019 | 0x1020 | N |  |  | Y | 0x8019 | 0x1020 | N |  |  | Y | 0x8019 | 0x1020 | Y | 0x8019 | 0x1020 | Y | 0x8019 | 0x1020 | Y | 0x8019 | 0x1020 | N |  |  | Y | 0x8019 | 0x1020 | Y | 0x8019 | 0x1020 | N |  |  | Y | 0x8019 | 0x1020
Cell 2 Voltage N: 1-32 | V | 0xA751+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1021 | Y | 0x8019 | 0x1021 | N |  |  | N |  |  | Y | 0x8019 | 0x1021 | Y | 0x8019 | 0x1021 | N |  |  | Y | 0x8019 | 0x1021 | N |  |  | Y | 0x8019 | 0x1021 | Y | 0x8019 | 0x1021 | Y | 0x8019 | 0x1021 | Y | 0x8019 | 0x1021 | N |  |  | Y | 0x8019 | 0x1021 | Y | 0x8019 | 0x1021 | N |  |  | Y | 0x8019 | 0x1021
Cell 3 Voltage N: 1-32 | V | 0xA752+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1022 | Y | 0x8019 | 0x1022 | N |  |  | N |  |  | Y | 0x8019 | 0x1022 | Y | 0x8019 | 0x1022 | N |  |  | Y | 0x8019 | 0x1022 | N |  |  | Y | 0x8019 | 0x1022 | Y | 0x8019 | 0x1022 | Y | 0x8019 | 0x1022 | Y | 0x8019 | 0x1022 | N |  |  | Y | 0x8019 | 0x1022 | Y | 0x8019 | 0x1022 | N |  |  | Y | 0x8019 | 0x1022
Cell 4 Voltage N: 1-32 | V | 0xA753+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1023 | Y | 0x8019 | 0x1023 | N |  |  | N |  |  | Y | 0x8019 | 0x1023 | Y | 0x8019 | 0x1023 | N |  |  | Y | 0x8019 | 0x1023 | N |  |  | Y | 0x8019 | 0x1023 | Y | 0x8019 | 0x1023 | Y | 0x8019 | 0x1023 | Y | 0x8019 | 0x1023 | N |  |  | Y | 0x8019 | 0x1023 | Y | 0x8019 | 0x1023 | N |  |  | Y | 0x8019 | 0x1023
Cell 5 Voltage N: 1-32 | V | 0xA754+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1024 | Y | 0x8019 | 0x1024 | N |  |  | N |  |  | Y | 0x8019 | 0x1024 | Y | 0x8019 | 0x1024 | N |  |  | Y | 0x8019 | 0x1024 | N |  |  | Y | 0x8019 | 0x1024 | Y | 0x8019 | 0x1024 | Y | 0x8019 | 0x1024 | Y | 0x8019 | 0x1024 | N |  |  | Y | 0x8019 | 0x1024 | Y | 0x8019 | 0x1024 | N |  |  | Y | 0x8019 | 0x1024
Cell 6 Voltage N: 1-32 | V | 0xA755+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1025 | Y | 0x8019 | 0x1025 | N |  |  | N |  |  | Y | 0x8019 | 0x1025 | Y | 0x8019 | 0x1025 | N |  |  | Y | 0x8019 | 0x1025 | N |  |  | Y | 0x8019 | 0x1025 | Y | 0x8019 | 0x1025 | Y | 0x8019 | 0x1025 | Y | 0x8019 | 0x1025 | N |  |  | Y | 0x8019 | 0x1025 | Y | 0x8019 | 0x1025 | N |  |  | Y | 0x8019 | 0x1025
Cell 7 Voltage N: 1-32 | V | 0xA756+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1026 | Y | 0x8019 | 0x1026 | N |  |  | N |  |  | Y | 0x8019 | 0x1026 | Y | 0x8019 | 0x1026 | N |  |  | Y | 0x8019 | 0x1026 | N |  |  | Y | 0x8019 | 0x1026 | Y | 0x8019 | 0x1026 | Y | 0x8019 | 0x1026 | Y | 0x8019 | 0x1026 | N |  |  | Y | 0x8019 | 0x1026 | Y | 0x8019 | 0x1026 | N |  |  | Y | 0x8019 | 0x1026
Cell 8 Voltage N: 1-32 | V | 0xA757+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1027 | Y | 0x8019 | 0x1027 | N |  |  | N |  |  | Y | 0x8019 | 0x1027 | Y | 0x8019 | 0x1027 | N |  |  | Y | 0x8019 | 0x1027 | N |  |  | Y | 0x8019 | 0x1027 | Y | 0x8019 | 0x1027 | Y | 0x8019 | 0x1027 | Y | 0x8019 | 0x1027 | N |  |  | Y | 0x8019 | 0x1027 | Y | 0x8019 | 0x1027 | N |  |  | Y | 0x8019 | 0x1027
Cell 9 Voltage N: 1-32 | V | 0xA758+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1028 | Y | 0x8019 | 0x1028 | N |  |  | N |  |  | Y | 0x8019 | 0x1028 | Y | 0x8019 | 0x1028 | N |  |  | Y | 0x8019 | 0x1028 | N |  |  | Y | 0x8019 | 0x1028 | Y | 0x8019 | 0x1028 | Y | 0x8019 | 0x1028 | Y | 0x8019 | 0x1028 | N |  |  | Y | 0x8019 | 0x1028 | Y | 0x8019 | 0x1028 | N |  |  | Y | 0x8019 | 0x1028
Cell 10 Voltage N: 1-32 | V | 0xA759+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x1029 | Y | 0x8019 | 0x1029 | N |  |  | N |  |  | Y | 0x8019 | 0x1029 | Y | 0x8019 | 0x1029 | N |  |  | Y | 0x8019 | 0x1029 | N |  |  | Y | 0x8019 | 0x1029 | Y | 0x8019 | 0x1029 | Y | 0x8019 | 0x1029 | Y | 0x8019 | 0x1029 | N |  |  | Y | 0x8019 | 0x1029 | Y | 0x8019 | 0x1029 | N |  |  | Y | 0x8019 | 0x1029
Cell 11 Voltage N: 1-32 | V | 0xA75A+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x102A | Y | 0x8019 | 0x102A | N |  |  | N |  |  | Y | 0x8019 | 0x102A | Y | 0x8019 | 0x102A | N |  |  | Y | 0x8019 | 0x102A | N |  |  | Y | 0x8019 | 0x102A | Y | 0x8019 | 0x102A | Y | 0x8019 | 0x102A | Y | 0x8019 | 0x102A | N |  |  | Y | 0x8019 | 0x102A | Y | 0x8019 | 0x102A | N |  |  | Y | 0x8019 | 0x102A
Cell 12 Voltage N: 1-32 | V | 0xA75B+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x102B | Y | 0x8019 | 0x102B | N |  |  | N |  |  | Y | 0x8019 | 0x102B | Y | 0x8019 | 0x102B | N |  |  | Y | 0x8019 | 0x102B | N |  |  | Y | 0x8019 | 0x102B | Y | 0x8019 | 0x102B | Y | 0x8019 | 0x102B | Y | 0x8019 | 0x102B | N |  |  | Y | 0x8019 | 0x102B | Y | 0x8019 | 0x102B | N |  |  | Y | 0x8019 | 0x102B
Cell 13 Voltage N: 1-32 | V | 0xA75C+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x102C | Y | 0x8019 | 0x102C | N |  |  | N |  |  | Y | 0x8019 | 0x102C | Y | 0x8019 | 0x102C | N |  |  | Y | 0x8019 | 0x102C | N |  |  | Y | 0x8019 | 0x102C | Y | 0x8019 | 0x102C | Y | 0x8019 | 0x102C | Y | 0x8019 | 0x102C | N |  |  | Y | 0x8019 | 0x102C | Y | 0x8019 | 0x102C | N |  |  | Y | 0x8019 | 0x102C
Cell 14 Voltage N: 1-32 | V | 0xA75D+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x102D | Y | 0x8019 | 0x102D | N |  |  | N |  |  | Y | 0x8019 | 0x102D | Y | 0x8019 | 0x102D | N |  |  | Y | 0x8019 | 0x102D | N |  |  | Y | 0x8019 | 0x102D | Y | 0x8019 | 0x102D | Y | 0x8019 | 0x102D | Y | 0x8019 | 0x102D | N |  |  | Y | 0x8019 | 0x102D | Y | 0x8019 | 0x102D | N |  |  | Y | 0x8019 | 0x102D
Cell 15 Voltage N: 1-32 | V | 0xA75E+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x102E | Y | 0x8019 | 0x102E | N |  |  | N |  |  | Y | 0x8019 | 0x102E | Y | 0x8019 | 0x102E | N |  |  | Y | 0x8019 | 0x102E | N |  |  | Y | 0x8019 | 0x102E | Y | 0x8019 | 0x102E | Y | 0x8019 | 0x102E | Y | 0x8019 | 0x102E | N |  |  | Y | 0x8019 | 0x102E | Y | 0x8019 | 0x102E | N |  |  | Y | 0x8019 | 0x102E
Cell 16 Voltage N: 1-32 | V | 0xA75F+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x102F | Y | 0x8019 | 0x102F | N |  |  | N |  |  | Y | 0x8019 | 0x102F | Y | 0x8019 | 0x102F | N |  |  | Y | 0x8019 | 0x102F | N |  |  | Y | 0x8019 | 0x102F | Y | 0x8019 | 0x102F | Y | 0x8019 | 0x102F | Y | 0x8019 | 0x102F | N |  |  | Y | 0x8019 | 0x102F | Y | 0x8019 | 0x102F | N |  |  | Y | 0x8019 | 0x102F
Cell 17 Voltage N: 1-32 | V | 0xA760+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x10B6 | Y | 0x8019 | 0x10B6 | N |  |  | N |  |  | Y | 0x8019 | 0x10B6 | Y | 0x8019 | 0x10B6 | N |  |  | Y | 0x8019 | 0x10B6 | N |  |  | Y | 0x8019 | 0x10B6 | Y | 0x8019 | 0x10B6 | Y | 0x8019 | 0x10B6 | Y | 0x8019 | 0x10B6 | N |  |  | Y | 0x8019 | 0x10B6 | Y | 0x8019 | 0x10B6 | N |  |  | Y | 0x8019 | 0x10B6
Cell 18 Voltage N: 1-32 | V | 0xA761+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x10B7 | Y | 0x8019 | 0x10B7 | N |  |  | N |  |  | Y | 0x8019 | 0x10B7 | Y | 0x8019 | 0x10B7 | N |  |  | Y | 0x8019 | 0x10B7 | N |  |  | Y | 0x8019 | 0x10B7 | Y | 0x8019 | 0x10B7 | Y | 0x8019 | 0x10B7 | Y | 0x8019 | 0x10B7 | N |  |  | Y | 0x8019 | 0x10B7 | Y | 0x8019 | 0x10B7 | N |  |  | Y | 0x8019 | 0x10B7
Cell 19 Voltage N: 1-32 | V | 0xA762+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x10B8 | Y | 0x8019 | 0x10B8 | N |  |  | N |  |  | Y | 0x8019 | 0x10B8 | Y | 0x8019 | 0x10B8 | N |  |  | Y | 0x8019 | 0x10B8 | N |  |  | Y | 0x8019 | 0x10B8 | Y | 0x8019 | 0x10B8 | Y | 0x8019 | 0x10B8 | Y | 0x8019 | 0x10B8 | N |  |  | Y | 0x8019 | 0x10B8 | Y | 0x8019 | 0x10B8 | N |  |  | Y | 0x8019 | 0x10B8
Cell 20 Voltage N: 1-32 | V | 0xA763+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x10B9 | Y | 0x8019 | 0x10B9 | N |  |  | N |  |  | Y | 0x8019 | 0x10B9 | Y | 0x8019 | 0x10B9 | N |  |  | Y | 0x8019 | 0x10B9 | N |  |  | Y | 0x8019 | 0x10B9 | Y | 0x8019 | 0x10B9 | Y | 0x8019 | 0x10B9 | Y | 0x8019 | 0x10B9 | N |  |  | Y | 0x8019 | 0x10B9 | Y | 0x8019 | 0x10B9 | N |  |  | Y | 0x8019 | 0x10B9
Cell 21 Voltage N: 1-32 | V | 0xA764+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x10BA | Y | 0x8019 | 0x10BA | N |  |  | N |  |  | Y | 0x8019 | 0x10BA | Y | 0x8019 | 0x10BA | N |  |  | Y | 0x8019 | 0x10BA | N |  |  | Y | 0x8019 | 0x10BA | Y | 0x8019 | 0x10BA | Y | 0x8019 | 0x10BA | Y | 0x8019 | 0x10BA | N |  |  | Y | 0x8019 | 0x10BA | Y | 0x8019 | 0x10BA | N |  |  | Y | 0x8019 | 0x10BA
Cell 22 Voltage N: 1-32 | V | 0xA765+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x10BB | Y | 0x8019 | 0x10BB | N |  |  | N |  |  | Y | 0x8019 | 0x10BB | Y | 0x8019 | 0x10BB | N |  |  | Y | 0x8019 | 0x10BB | N |  |  | Y | 0x8019 | 0x10BB | Y | 0x8019 | 0x10BB | Y | 0x8019 | 0x10BB | Y | 0x8019 | 0x10BB | N |  |  | Y | 0x8019 | 0x10BB | Y | 0x8019 | 0x10BB | N |  |  | Y | 0x8019 | 0x10BB
Battery String SOH N: 1-32 | % | 0xA766+(N-1)*64 | UINT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8019 | 0x1032 | Y | 0x8019 | 0x1032 | N | 0x8019 | 0x1032 | N |  |  | Y | 0x8019 | 0x1032 | Y | 0x8019 | 0x1032 | N | 0x8019 | 0x1032 | N |  |  | Y | 0x8019 | 0x1032 | Y | 0x8019 | 0x1032 | Y | 0x8019 | 0x1032 | N | 0x8019 | 0x1032 | N | 0x8019 | 0x1032 | Y | 0x8019 | 0x1032 | Y | 0x8019 | 0x1032 | N | 0x8019 | 0x1032 | Y | 0x8019 | 0x1032 | Y | 0x8019 | 0x1032 | N | 0x8019 | 0x1032
Battery State N: 1-32 | NA | 0xA767+(N-1)*64 | UINT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | Y | 0x8019 | 0x1035 | N | 0x8019 | 0x1035 | N |  |  | N |  |  | Y | 0x8019 | 0x1035 | N | 0x8019 | 0x1035 | N |  |  | Y | 0x8019 | 0x1035 | N |  |  | Y | 0x8019 | 0x1035 | N | 0x8019 | 0x1035 | N | 0x8019 | 0x1035 | Y | 0x8019 | 0x1035 | N |  |  | N | 0x8019 | 0x1035 | Y | 0x8019 | 0x1035 | N |  |  | N | 0x8019 | 0x1035
BMU Address N: 1-32 | NA | 0xA768+(N-1)*64 | UINT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | Y | 0x8019 | 0x1033 | N | 0x8019 | 0x1033 | N |  |  | N |  |  | Y | 0x8019 | 0x1033 | N | 0x8019 | 0x1033 | N |  |  | Y | 0x8019 | 0x1033 | N |  |  | Y | 0x8019 | 0x1033 | N | 0x8019 | 0x1033 | N | 0x8019 | 0x1033 | Y | 0x8019 | 0x1033 | N |  |  | N | 0x8019 | 0x1033 | Y | 0x8019 | 0x1033 | N |  |  | N | 0x8019 | 0x1033
Capacity N: 1-32 | Ah | 0xA769~0xA76A+(N-1)*64 | UINT32 | 4 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | Y | 0x8019 | 0x1036 | N | 0x8019 | 0x1036 | N |  |  | N |  |  | Y | 0x8019 | 0x1036 | N | 0x8019 | 0x1036 | N |  |  | Y | 0x8019 | 0x1036 | N |  |  | Y | 0x8019 | 0x1036 | N | 0x8019 | 0x1036 | N | 0x8019 | 0x1036 | Y | 0x8019 | 0x1036 | N |  |  | N | 0x8019 | 0x1036 | Y | 0x8019 | 0x1036 | N |  |  | N | 0x8019 | 0x1036
Output Power N: 1-32 | W | 0xA76B+(N-1)*64 | UINT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | Y | 0x8019 | 0x1065 | N | 0x8019 | 0x1065 | N |  |  | N |  |  | Y | 0x8019 | 0x1065 | N | 0x8019 | 0x1065 | N |  |  | Y | 0x8019 | 0x1065 | N |  |  | Y | 0x8019 | 0x1065 | N | 0x8019 | 0x1065 | N | 0x8019 | 0x1065 | Y | 0x8019 | 0x1065 | N |  |  | N | 0x8019 | 0x1065 | Y | 0x8019 | 0x1065 | N |  |  | N | 0x8019 | 0x1065
Work Status N: 1-32 | NA | 0xA76C+(N-1)*64 | UINT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | Y | 0x8019 | 0x1074 | N | 0x8019 | 0x1074 | N |  |  | N |  |  | Y | 0x8019 | 0x1074 | N | 0x8019 | 0x1074 | N |  |  | Y | 0x8019 | 0x1074 | N |  |  | Y | 0x8019 | 0x1074 | N | 0x8019 | 0x1074 | N | 0x8019 | 0x1074 | Y | 0x8019 | 0x1074 | N |  |  | N | 0x8019 | 0x1074 | Y | 0x8019 | 0x1074 | N |  |  | N | 0x8019 | 0x1074
Cells Number N: 1-32 | NA | 0xA76D+(N-1)*64 | UINT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x2016 | Y | 0x8019 | 0x2016 | N |  |  | N |  |  | Y | 0x8019 | 0x2016 | Y | 0x8019 | 0x2016 | N |  |  | Y | 0x8019 | 0x2016 | N |  |  | Y | 0x8019 | 0x2016 | Y | 0x8019 | 0x2016 | Y | 0x8019 | 0x2016 | Y | 0x8019 | 0x2016 | N |  |  | Y | 0x8019 | 0x2016 | Y | 0x8019 | 0x2016 | N |  |  | Y | 0x8019 | 0x2016
Cell 23 Temperature N: 1-32 | degC | 0xA76E+(N-1)*64 | INT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x10AC | Y | 0x8019 | 0x10AC | N |  |  | N |  |  | Y | 0x8019 | 0x10AC | Y | 0x8019 | 0x10AC | N |  |  | Y | 0x8019 | 0x10AC | N |  |  | Y | 0x8019 | 0x10AC | Y | 0x8019 | 0x10AC | Y | 0x8019 | 0x10AC | Y | 0x8019 | 0x10AC | N |  |  | Y | 0x8019 | 0x10AC | Y | 0x8019 | 0x10AC | N |  |  | Y | 0x8019 | 0x10AC
Cell 23 Voltage N: 1-32 | V | 0xA76F+(N-1)*64 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x10BC | Y | 0x8019 | 0x10BC | N |  |  | N |  |  | Y | 0x8019 | 0x10BC | Y | 0x8019 | 0x10BC | N |  |  | Y | 0x8019 | 0x10BC | N |  |  | Y | 0x8019 | 0x10BC | Y | 0x8019 | 0x10BC | Y | 0x8019 | 0x10BC | Y | 0x8019 | 0x10BC | N |  |  | Y | 0x8019 | 0x10BC | Y | 0x8019 | 0x10BC | N |  |  | Y | 0x8019 | 0x10BC
Battery Type N: 1-32 | NA | 0xA770 +(N-1)*64 | UINT16 | 2 | 0 | [ESU-A=0]/[ESM-BX=1]/[ESM-A=2]/[ESM-4810A1=3]/[DBU=4] | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers Reserved (0xAF31~0xAFFF) | [23 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Amount | NA | 0xD000 | UINT16 | 2 | 0 | Summarizes the number of bypass modules at the system level. 4 in maximum |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Amount | NA | 0xD001 | UINT16 | 2 | 0 | Summarizes the number of inverter unit modules at the system level. 4 in maximum |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Amount | NA | 0xD002 | UINT16 | 2 | 0 | Summarizes the number of inverter modules at the system level. 32 in maximum |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
ECM Amount | NA | 0xD003 | UINT16 | 2 | 0 | Summarizes the number of ECM modules at the system level. 8 in maximum |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Amount | NA | 0xD004 | UINT16 | 2 | 0 | Summarizes the number of extend distribution frame modules at the system level. 32 in maximum |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers Reserved (0xD005~0xD00F) | [13 empty] | N | [9 empty] | N | [8 empty] | N |  |  | N | [8 empty] | N |  |  | N |  |  | N | [14 empty] | N | [8 empty] | N
Bypass Input Voltage N:1-4 | V | 0xD010+(N-1)*16 | UINT16 | 2 | 1 | invalid if the system is three-phase. |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Phase L1 Voltage N:1-4 | V | 0xD011+(N-1)*16 | UINT16 | 2 | 1 | invalid if the system is single-phase. |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Phase L2 Voltage N:1-4 | V | 0xD012+(N-1)*16 | UINT16 | 2 | 1 | invalid if the system is single-phase. |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Phase L3 Voltage N:1-4 | V | 0xD013+(N-1)*16 | UINT16 | 2 | 1 | invalid if the system is single-phase. |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Input Freqency N:1-4 | Hz | 0xD014+(N-1)*16 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Temperature N:1-4 | degC | 0xD015+(N-1)*16 | INT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Air Intake Temperature N:1-4 | degC | 0xD016+(N-1)*16 | INT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Work State N:1-4 | NA | 0xD017+(N-1)*16 | UINT16 | 2 | 0 | [On=0]/[Off=1] |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers Reserved (0xD018~0xD01F+(N-1)*16) | [23 empty] | N | [8 empty] | N |  |  | N | [8 empty] | N |  |  | N |  |  | N | [14 empty] | N | [8 empty] | N
[10 empty] | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Quantity of Inverters N:1-4 | pcs | 0xD050+(N-1)*32 | UINT16 | 2 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Input DC Voltage N:1-4 | V | 0xD051+(N-1)*32 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Input DC Current N:1-4 | A | 0xD052+(N-1)*32 | UINT32 | 4 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Input DC Power N:1-4 | kW | 0xD054+(N-1)*32 | UINT32 | 4 | 2 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Output Voltage N:1-4 | V | 0xD056+(N-1)*32 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Output Current N:1-4 | A | 0xD057+(N-1)*32 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit AC Frequency N:1-4 | Hz | 0xD058+(N-1)*32 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Phase L1 Voltage N:1-4 | V | 0xD059+(N-1)*32 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Phase L2 Voltage N:1-4 | V | 0xD05A+(N-1)*32 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Phase L3 Voltage N:1-4 | V | 0xD05B+(N-1)*32 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Phase L1 Current N:1-4 | A | 0xD05C+(N-1)*32 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Phase L2 Current N:1-4 | A | 0xD05D+(N-1)*32 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Phase L3 Current N:1-4 | A | 0xD05E+(N-1)*32 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Apparent Power N:1-4 | kVA | 0xD05F+(N-1)*32 | UINT32 | 4 | 2 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Load Rate | % | 0xD061+(N-1)*32 | UINT16 | 2 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers Reserved (0xD062~0xD06F+(N-1)*32) | [7 empty] | N | [5 empty] | N | [9 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Input DC Voltage N: 1-32 | V | 0xD0D0+(N-1)*16 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Input DC Current N: 1-32 | A | 0xD0D1+(N-1)*16 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Input DC Power N: 1-32 | kW | 0xD0D2+(N-1)*16 | UINT16 | 2 | 2 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Output Voltage N: 1-32 | V | 0xD0D3+(N-1)*16 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Output Current N: 1-32 | A | 0xD0D4+(N-1)*16 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Output Freqency N: 1-32 | Hz | 0xD0D5+(N-1)*16 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Output Active Power N: 1-32 | kW | 0xD0D6+(N-1)*16 | UINT16 | 2 | 2 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Output Apparent Power N: 1-32 | kVA | 0xD0D7+(N-1)*16 | UINT16 | 2 | 2 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Output Power Factor N: 1-32 | NA | 0xD0D8+(N-1)*16 | INT16 | 2 | 3 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Temperature N: 1-32 | degC | 0xD0D9+(N-1)*16 | INT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Work State N: 1-32 | NA | 0xD0DA+(N-1)*16 | UINT16 | 2 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Total Run Time N: 1-32 | h | 0xD0DB+(N-1)*16 | UINT16 | 2 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Phase N: 1-32 | NA | 0xD0DC+(N-1)*16 | UINT16 | 2 | 0 | [5 empty] | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers Reserved (0xD0DD~0xD0DF+(N-1)*16) | [7 empty] | N | [15 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers Reserved (0xD2C0~0xD2CF) | [7 empty] | N | [15 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU DC Voltage N:1-32 | V | 0xD2D0+(N-1)*32 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Total DC Load Current N:1-32 | A | 0xD2D1+(N-1)*32 | UINT32 | 4 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load1 Current N:1-32 | A | 0xD2D3+(N-1)*32 | UINT32 | 4 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load2 Current N:1-32 | A | 0xD2D5+(N-1)*32 | UINT32 | 4 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load3 Current N:1-32 | A | 0xD2D7+(N-1)*32 | UINT32 | 4 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load4 Current N:1-32 | A | 0xD2D9+(N-1)*32 | UINT32 | 4 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Total DC Load Energy Consumption N:1-32 | kWh | 0xD2DB+(N-1)*32 | UINT64 | 8 | 2 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load1 Energy Consumption N:1-32 | kWh | 0xD2DF+(N-1)*32 | UINT64 | 8 | 2 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load2 Energy Consumption N:1-32 | kWh | 0xD2E3+(N-1)*32 | UINT64 | 8 | 2 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load3 Energy Consumption N:1-32 | kWh | 0xD2E7+(N-1)*32 | UINT64 | 8 | 2 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load4 Energy Consumption N:1-32 | kWh | 0xD2EB+(N-1)*32 | UINT64 | 8 | 2 | [5 empty] | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers Reserved (0xD2EF~0xD2EF+(N-1)*32) | [7 empty] | N | [15 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
ECM Input DC Voltage N:1-8 | V | 0xD6D1+(N-1)*16 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
ECM Input DC Current N:1-8 | A | 0xD6D2+(N-1)*16 | UINT32 | 4 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
ECM Input DC Power N:1-8 | kW | 0xD6D4+(N-1)*16 | UINT16 | 2 | 2 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
ECM Output Voltage N:1-8 | V | 0xD6D5+(N-1)*16 | UINT16 | 2 | 1 | invalid if the system is three-phase. |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
ECM Output Current N:1-8 | A | 0xD6D6+(N-1)*16 | UINT16 | 2 | 1 | invalid if the system is single-phase. |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
ECM Output Freqency N:1-8 | Hz | 0xD6D7+(N-1)*16 | UINT16 | 2 | 1 | invalid if the system is single-phase. |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
ECM Output Apparent Power N:1-8 | kVA | 0xD6D8+(N-1)*16 | UINT16 | 2 | 2 | invalid if the system is single-phase. |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
ECM Work State N:1-8 | NA | 0xD6D9+(N-1)*16 | UINT16 | 2 | 0 | [Off=0]/[No-Output=1]/[Bypass=2]/[Inverting=3] |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers(0xD750~) | [23 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Amount | NA | 0xD750 | UINT16 | 2 | 0 | Summarizes the number of solar-storage modules at the system level. 4 in maximum |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Group DC Output Voltage | V | 0xD751 | UINT16 | 2 | 2 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Group Total Load Current | A | 0xD752 | INT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Group Battery Voltage | V | 0xD753 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Group Battery Current | A | 0xD754 | INT32 | 4 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Group Battery Total Capacity | Ah | 0xD756 | UINT32 | 4 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Group Remaining Battery Capacity Percent | % | 0xD758 | UINT16 | 2 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Group Battery Average Temperature | degC | 0xD759 | INT16 | 2 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers Reserved (0xD75A~0xD75F) | [23 empty] | N | [8 empty] | N |  |  | N | [8 empty] | N |  |  | N |  |  | N | [14 empty] | N | [8 empty] | N
SSM Battery Voltage N:1-4 | V | 0xD760+(N-1)*16 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Battery Current N:1-4 | A | 0xD761+(N-1)*16 | INT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Battery SOH N:1-4 | % | 0xD762+(N-1)*16 | UINT16 | 2 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Battery Capacity N:1-4 | Ah | 0xD763+(N-1)*16 | UINT32 | 4 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Remaining Battery Capacity Percent N:1-4 | % | 0xD765+(N-1)*16 | UINT16 | 2 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Cell1 Temperature N:1-4 | degC | 0xD766+(N-1)*16 | INT16 | 2 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Cell2 Temperature N:1-4 | degC | 0xD767+(N-1)*16 | INT16 | 2 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM 12V Port Output Voltage N:1-4 | V | 0xD768+(N-1)*16 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM 12V Port Output Current N:1-4 | A | 0xD769+(N-1)*16 | INT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Cell1 Voltage N:1-4 | V | 0xD76A+(N-1)*16 | UINT16 | 2 | 2 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Cell2 Voltage N:1-4 | V | 0xD76B+(N-1)*16 | UINT16 | 2 | 2 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM PV Input Voltage N:1-4 | V | 0xD76C+(N-1)*16 | UINT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM PV Input Current N:1-4 | A | 0xD76D+(N-1)*16 | INT16 | 2 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers Reserved (0xD76E~0xD76F+(N-1)*16) | [23 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers(0xD7A0~) | [23 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DC Output Distribution Load-iCBD Amount | NA | 0xD7A0 | UINT16 | 2 | 0 | Load-iCBD maxinum number 62 | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DC Output Distribution Load-iCBD Existence flag | NA | 0xD7A1~0xD7A4 | UINT16*4 | 8 | 0 | 0xD7A1=0x0005,0xD7A2=0x0005,0xD7A3=0x0001,and 0xD7A4=0x0001means the Load-iCBD1/3/17/19/33/49 exist | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Registers Reversed for Load-iCBD Summary Information(0xD7A5~0xD7AF)
DC Output Distribution Load-iCBD current N:1~62 | A | 0xD7B0~0xD7B1+(N-1)*12 | INT32 | 4 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DC Output Distribution Load-iCBD Power Consumption N:1~62 | kWh | 0xD7B2~0xD7B3+(N-1)*12 | UINT32 | 4 | 2 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DC Output Distribution Load-iCBD Power N:1~62 | kW | 0xD7B4~0xD7B5+(N-1)*12 | UINT32 | 4 | 2 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DC Output Distribution Load-iCBD Rated Capacity N:1~62 | A | 0xD7B6~0xD7B7+(N-1)*12 | INT32 | 4 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Registers Reversed for DC Output Distribution Load-iCBD Information(0xD7B8~0xD7BB+(N-1)*12) max address:0xDA97
Registers (0xDA98~0xDBAF) can be used
Branch Group Amount | NA | 0xDBB0 | UINT16 | 2 | 0 | Branch Group maxinum number
Branch Group Existence flag | NA | 0xDBB1~0xDBB2 | UINT16*2 | 4 | 0
Registers Reversed for Branch Group Summary Information(0xDBB3~0xDBBF)
Branch Group current N:1~30 | A | 0xDBC0~0xDBC1+(N-1)*16 | INT32 | 4 | 1
Branch Group Power Consumption N:1~30 | kWh | 0xDBC2~0xDBC3+(N-1)*16 | UINT32 | 4 | 2
Registers Reversed for Branch Group Information(0xDBC4~0xDBCF+(N-1)*16) max address:0xDD9F
DC Output Distribution Amount | NA | 0xDDA0 | UINT16 | 2 | 0 | DC Output Distribution maxinum number
DC Output Distribution Existence flag | NA | 0xDDA1~0xDDA3 | UINT16*3 | 6 | 0
Registers Reversed for DC Output Distribution Summary Information(0xDDA4~0xDDAF)
DC Output Distribution current N:1~8 | A | 0xDDB0~0xDDB1+(N-1)*16 | INT32 | 4 | 1
DC Output Distribution Power Consumption N:1~8 | kWh | 0xDDB2~0xDDB3+(N-1)*16 | UINT32 | 4 | 2
Registers Reversed for DC Output Distribution Information(0xDDB4~0xDDBF+(N-1)*16) max address:0xDE2F
24V Module Amount | NA | 0xDE30 | UINT16 | 2 | 0 | 24V Module maxinum number | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
24V Module Existence flag | NA | 0xDE31 | UINT16 | 2 | 0 | If the 24V module exists, the corresponding bit is set to 1. 0x0005 means the 1th and 3th module exist, the 24V Module Amount is 2. | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
24V Module Group Output Voltage | V | 0xDE32 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
24V Module Group Total Output Current | A | 0xDE33 | UINT32 | 4 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
24V Module Group Total Output Power | W | 0xDE35 | UINT32 | 4 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Registers Reversed(0xDE37~0xDE3F)
24V Module Output Voltage N:1~8 | V | 0xDE40+(N-1)*8 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
24V Module Output Current N:1~8 | A | 0xDE41+(N-1)*8 | UINT32 | 4 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
24V Module Output Power N:1~8 | W | 0xDE43+(N-1)*8 | UINT32 | 4 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Registers Reversed(0xDE45~0xDE47)
Registers(0xDE80~0xDFFF) can be used
iDMU Amount | NA | 0xC000 | UINT16 | 2 | 0 | iDMU maxinum number 4 | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDMU Existence flag | NA | 0xC001 | UINT16 | 2 | 0 | 0x0005 means the iDMU1 and iDMU3 exist
iDMU M Load-iCBD Amount M:1~4 | NA | 0xC002~0xC003 | UINT16*2 | 4 | 0 | iDMU Load-iCBD maxinum number 34 0xC002 high 8bit is iDMU2, low 8bit is iDMU1,0xC003 high 8bit is iDMU4, low 8bit is iDMU3 | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDMU M Load-iCBD N Existence flag M:1~4 N:1-34 | NA | 0xC004~0xC006+(M-1)*3 | UINT16*3 | 6 | 0 | 0xC004=0x0005,0xC005=0x0005 and 0xC006=0x0001means the iDMU1 Load-iCBD1/3/17/19/33exist | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDMU M Load-iCBD N current M:1~4 N:1-34 | A | 0xC010~0xC011+(M-1)*408+(N-1)*12 | INT32 | 4 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDMU M Load-iCBD N Power Consumption M:1~4 N:1-34 | kWh | 0xC012~0xC013+(M-1)*408+(N-1)*12 | UINT32 | 4 | 2 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDMU M Load-iCBD N Power M:1~4 N:1-34 | kW | 0xC014~0xC015+(M-1)*408+(N-1)*12 | UINT32 | 4 | 2 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDMU M Load-iCBD N Rated Capacity M:1~4 N:1-34 | A | 0xC016~0xC017+(M-1)*408+(N-1)*12 | INT32 | 4 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Registers Reversed for iDMU ULoad-iCBD Information(0xC018~0xC01B+(N-1)*12) max address:0xC66F
Battery Barcode N: 1-32 |  | 0xC670~0xC67E+(N-1)*32 | STRING | 30 | 0 | BMU Barcode | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Software Version N: 1-32 |  | 0xC67F~0xC681+(N-1)*32 | STRING | 5 | 0 | Software Version | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Hardware Version N: 1-32 |  | 0xC682~0xC684+(N-1)*32 | STRING | 5 | 0 | Hardware Version | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Registers Reserved For ACB: 0xC685~0xC68F+(N-1)*32
PV Adapter 1–N (N=18) Address | NA | 0xCA70+(N-1)*32 | UINT16 | 2 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x81D5 | 0x100A | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
PV Adapter1–N (N=18) Running State | NA | 0xCA71+(N-1)*32 | UINT16 | 2 | NA | 0: ON 1: OFF | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x81D5 | 0x1006 | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
PV Adapter 1–N (N=18) Input Voltage | V | 0xCA72+(N-1)*32 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x81D5 | 0x1003 | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
PV Adapter 1–N (N=18) Input Current | A | 0xCA73+(N-1)*32 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x81D5 | to add | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
PV Adapter 1–N (N=18) Output Voltage | V | 0xCA74+(N-1)*32 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x81D5 | 0x1001 | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
PV Adapter 1–N (N=18) Output Current | A | 0xCA75+(N-1)*32 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x81D5 | 0x1002 | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
PV Adapter 1–N (N=18) Temperature | ℃ | 0xCA76+(N-1)*32 | UINT16 | 2 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x81D5 | 0x1005 | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
PV Adapter 1–N (N=18) Output Power | kW | 0xCA77~0xCA78+(N-1)*32 | UINT32 | 4 | 2 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x81D5 | 0x100E | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
PV Adapter 1–N (N=18) Software Version | NA | 0xCA79~0xCA81+(N-1)*32 | STRING | 18 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x81D5 | 0x1010 | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
PV Adapter 1–N (N=18) Type | NA | 0xCA82~0xCA8A+(N-1)*32 | STRING | 18 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x81D5 | to add | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Registers Reserved(0xCCAB~0xCCAF)for other PV Adapter
Registers(0xCCB0~0xCFFF)
Note on U263: dongbeibei: 21B TR5-2支持
Note on W263: dongbeibei: 21B TR5-2支持
Note on X263: dongbeibei: 21B TR5-2支持
Note on Z263: dongbeibei: 21B TR5-2支持
Note on AG263: dongbeibei: 21B TR5-2支持
Note on AS263: dongbeibei: 21B TR5-2支持
Note on BH263: dongbeibei: 21B TR5-2支持
Note on BK263: dongbeibei: 21B TR5-2支持
Note on BT263: dongbeibei: 21B TR5-2支持
Note on CC263: dongbeibei: 21B TR5-2支持
Note on U277: dongbeibei: 21B TR5-2支持，一下ACB电池信息
Note on W277: dongbeibei: 21B TR5-2支持，一下ACB电池信息
Note on X277: dongbeibei: 21B TR5-2支持，一下ACB电池信息
Note on Z277: dongbeibei: 21B TR5-2支持，一下ACB电池信息
Note on AG277: dongbeibei: 21B TR5-2支持，一下ACB电池信息
Note on AS277: dongbeibei: 21B TR5-2支持，一下ACB电池信息
Note on BH277: dongbeibei: 21B TR5-2支持，一下ACB电池信息
Note on BK277: dongbeibei: 21B TR5-2支持，一下ACB电池信息
Note on BT277: dongbeibei: 21B TR5-2支持，一下ACB电池信息
Note on CC277: dongbeibei: 21B TR5-2支持，一下ACB电池信息

## Configuration Parameters
Data | Default Value | Lower Threshold | Upper Threshold | Unit | Register Address | Data Type | Precision | Remarks | SMU05A V500R001 C30/C50/C60 | SMU02B V300R002 C10/C20 | SMU02B V300R003 C00/C10 | SMU02B V500R001 C00/C10/C20/C30/C50/C60 | SMU02B V500R002 C00 | SMU02B V500R003 C10 | SCC800 V100R001C90 | SMU11D V500R002C50 | SMU V500R003C00(DPS) | SMU11B V500R003 C00 | SMU V500R003C10(DPS) | SMU11B V500R003 C10 | iSitePower V100R021C10(DPS) | iSitePower V100R021C10 (SMU02C/X) | iSitePower V100R021C10 (SMU11B) | iSitePower V100R021C10 (Solar cabinet) | iSitePower V100R021C91 (SMU02C/02X) | iSitePower V100R021C91 (PC510-IOT) | iSitePower V100R021C80 (SMU02C/02X) | DP-SP V300R022C00(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C00(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C00(SMU02C/02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C00 (SMU11B) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(SMU02C/02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10 (SMU11B) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(PVPU) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C00(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C00(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C00(SMU02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | iSitePower V100R023C92(SMU02C/02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C10(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C00(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C00(SMU02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C10(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C10(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C10(SMU02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value)
Year |  | 2000 | 2037 | NA | 0x2000 | UINT16 | 0 | Register 0x2000 ~ 0x2005 must be operated together, the threshold is UTC time | Y | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | N | Y | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | -
Month |  | 1 | 12 | NA | 0x2001 | UINT16 | 0 | Register 0x2000 ~ 0x2005 must be operated together, the threshold is UTC time | Y | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | N | Y | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | -
Day |  | 1 | 31 | NA | 0x2002 | UINT16 | 0 | Register 0x2000 ~ 0x2005 must be operated together, the threshold is UTC time | Y | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | N | Y | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | -
Hour |  | 0 | 23 | NA | 0x2003 | UINT16 | 0 | Register 0x2000 ~ 0x2005 must be operated together, the threshold is UTC time | Y | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | N | Y | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | -
Minute |  | 0 | 59 | NA | 0x2004 | UINT16 | 0 | Register 0x2000 ~ 0x2005 must be operated together, the threshold is UTC time | Y | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | N | Y | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | -
Second |  | 0 | 59 | NA | 0x2005 | UINT16 | 0 | Register 0x2000 ~ 0x2005 must be operated together, the threshold is UTC time | Y | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | N | Y | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | - | Y | - | -
[5 empty] | Registers Reserved | [10 empty] | N | [9 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Device Address | 33 | 1 | 255 | NA | 0x2010 | UINT16 | 0 |  | N | Y | Y | Y | Y | Y | N | N | Y | Y | Y | Y | Y | Y | Y | Y | Y | N | Y | Y | 0x8001 | 0x2814 | Y | 0x8001 | 0x2814 | Y | 0x8001 | 0x2814 | Y | 0x8001 | 0x2814 | Y | 0x8001 | 0x2814 | Y | 0x8001 | 0x2814 | Y | 0x8001 | 0x2814 | Y | 0x8001 | 0x2814 | Y | 0x8001 | 0x2814 | Y | 0x8001 | 0x2814 | Y | 0x8001 | 0x2814 | Y | 0x8001 | 0x2814 | Y | 0x8001 | 0x2814 | Y | 0x8001 | 0x2814 | Y | 0x8001 | 0x2814 | Y | 0x8001 | 0x2814 | Y | 0x8001 | 0x2814 | Y | 0x8001 | 0x2814 | Y | 0x8001 | 0x2814
[5 empty] | Registers Reserved | [20 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Control Mode | 0 | 0 | 1 | NA | 0x2050 | UINT16 | 0 | [Auto=0],[Manual=1] | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x2101 | Y | 0x8232 | 0x2101 | N |  |  | N |  |  | Y | 0x8001 | 0x2101 | Y | 0x8232 | 0x2101 | N |  |  | N |  |  | Y | 0x8001 | 0x2101 | Y | 0x8001 | 0x2101 | Y | 0x8232 | 0x2101 | N |  |  | N |  |  | Y | 0x8232 | 0x2101 | Y | 0x8001 | 0x2101 | N |  |  | Y | 0x8232 | 0x2101 | Y | 0x8001 | 0x2101 | N
[5 empty] | Registers Reserved | [20 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
DG Start Voltage | 47.5 | 35 | 58 | V | 0x2060 | UINT16 | 1 | [8 empty] | N |  | N | [7 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG Stop Voltage | 52.5 | 42 | 58 | V | 0x2061 | UINT16 | 1 | [8 empty] | N |  | N | [7 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG DOD to Start | 60 | 5 | 90 | % | 0x2062 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
[5 empty] | Registers Reserved | [20 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
site ID |  |  |  | NA | 0x2070~0x2073 | STRING | 0 | for 4 registers | [8 empty] | Y | N | Y |  | Y |  |  |  |  | N |  | Y | 0x8001 | 0x2180 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2180 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2180 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2180 | N |  |  | N |  |  | Y | 0x8001 | 0x2180 | N
[5 empty] | Registers(0x2074~0x207F) Reserved | [20 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Input DC Over Volt | 288 | 60 | 500 | V | 0x2080 | UINT16 | 0 | [9 empty] | Y | N | Y |  | Y |  |  |  |  | N |  | Y | 0x8001 | 0x262B | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x262B | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x262B | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x262B | N |  |  | N |  |  | Y | 0x8001 | 0x262B | N
Input DC Under Volt | 192 | 60 | 500 | V | 0x2081 | UINT16 | 0 | [9 empty] | Y | N | Y |  | Y |  |  |  |  | N |  | Y | 0x8001 | 0x262C | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x262C | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x262C | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x262C | N |  |  | N |  |  | Y | 0x8001 | 0x262C | N
[5 empty] | Registers Reserved | [20 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Rectifier Default Output Volt | 53.5 | 48 | 58 | V | 0x2090 | UINT16 | 1 | [9 empty] | Y | N | Y |  | Y |  |  |  |  | N |  | Y | 0x8003 | 0x2034 | Y | 0x8003 | 0x2034 | N |  |  | N |  |  | Y | 0x8003 | 0x2034 | Y | 0x8003 | 0x2034 | N |  |  | N |  |  | N |  |  | Y | 0x8003 | 0x2034 | Y | 0x8003 | 0x2034 | N |  |  | N |  |  | Y | 0x8003 | 0x2034 | Y | 0x8003 | 0x2034 | N |  |  | Y | 0x8003 | 0x2034 | Y | 0x8003 | 0x2034 | N
Low Rectifier Remaining Capacity | 75 | 0 | 150 | % | 0x2091 | UINT16 | 0 | [9 empty] | Y | N | Y |  | Y |  |  |  |  | N |  | Y | 0x8003 | 0x2015 | Y | 0x8003 | 0x2015 | N |  |  | N |  |  | Y | 0x8003 | 0x2015 | Y | 0x8003 | 0x2015 | N |  |  | N |  |  | N |  |  | Y | 0x8003 | 0x2015 | Y | 0x8003 | 0x2015 | N |  |  | N |  |  | Y | 0x8003 | 0x2015 | Y | 0x8003 | 0x2015 | N |  |  | Y | 0x8003 | 0x2015 | Y | 0x8003 | 0x2015 | N
[5 empty] | Registers Reserved | [20 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
DC Power Disconnect Voltage | 45 | 35 | 56 | V | 0x20A0 | UINT16 | 1 | [8 empty] | Y |  | N | [7 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
48V Port Setting Voltage | 48 | 53.5 | 55 | V | 0x20A1 | UINT16 | 1 | [8 empty] | Y |  | N | [7 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
57V DC Overvoltage Threshold | 73 | 58 | 75 | V | 0x20A2 | UINT16 | 1 | [8 empty] | Y |  | N | [7 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
57V DC Undervoltage Threshold | 53 | 50 | 59 | V | 0x20A3 | UINT16 | 1 | [8 empty] | Y |  | N | [7 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Dynamic Adjust Voltage Enabled | 0 | 0 | 1 | NA | 0x20A4 | UINT16 | 0 | [NO=0]/[YES=1] | [7 empty] | Y |  | N | [7 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AC Peak Shaving Enabled | 0 | 0 | 1 | NA | 0x20A5 | UINT16 | 0 | [NO=0]/[YES=1] | [7 empty] | Y |  | N | [7 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AC Capacity | 1000 | 1 | 10000 | A | 0x20A6 | UINT16 | 0 | [8 empty] | Y |  | N | [7 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AC Breaker Rated Current | 1000 | 1 | 10000 | kW | 0x20A7 | UINT16 | 0 | [8 empty] | Y |  | N | [7 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AC Derating Coefficient | 0.8 | 0.1 | 1 | NA | 0x20A8 | UINT16 | 1 | [8 empty] | Y |  | N | [7 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Rated AC Phase Voltage | 220 | 60 | 300 | V | 0x20A9 | UINT16 | 0 | [8 empty] | Y |  | N | [7 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
[5 empty] | Registers Reserved | [20 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
LLVD1 Enable | 1 | 0 | 1 | NA | 0x2100 | UINT16 | 0 | [NO=0]/[YES=1] | Y | Y | Y | Y | Y | Y | N | N |  | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x2102 | N |  |  | Y | 0x8001 | 0x2102 | Y | 0x8226 | 0x2102 | Y | 0x8001 | 0x2102 | N |  |  | Y | 0x8001 | 0x2102 | Y | 0x8226 | 0x2102 | N |  |  | Y | 0x8001 | 0x2102 | N |  |  | Y | 0x8001 | 0x2102 | Y | 0x8001 | 0x2102 | N |  |  | Y | 0x8001 | 0x2102 | Y | 0x8001 | 0x2102 | N |  |  | Y | 0x8001 | 0x2102 | Y | 0x8001 | 0x2102
LLVD1 Voltage | 45 | 36 | 56 | V | 0x2101 | UINT16 | 1 |  | Y | Y | Y | Y | Y | Y | N | N |  | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x2104 | N |  |  | Y | 0x8001 | 0x2104 | Y | 0x8226 | 0x2104 | Y | 0x8001 | 0x2104 | N |  |  | Y | 0x8001 | 0x2104 | Y | 0x8226 | 0x2104 | N |  |  | Y | 0x8001 | 0x2104 | N |  |  | Y | 0x8001 | 0x2104 | Y | 0x8001 | 0x2104 | N |  |  | Y | 0x8001 | 0x2104 | Y | 0x8001 | 0x2104 | N |  |  | Y | 0x8001 | 0x2104 | Y | 0x8001 | 0x2104
LLVD1 Connection Voltage | 51.5 | 37 | 58 | V | 0x2102 | UINT16 | 1 |  | Y | Y | Y | Y | Y | Y | N | N |  | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x2105 | N |  |  | Y | 0x8001 | 0x2105 | Y | 0x8226 | 0x2105 | Y | 0x8001 | 0x2105 | N |  |  | Y | 0x8001 | 0x2105 | Y | 0x8226 | 0x2105 | N |  |  | Y | 0x8001 | 0x2105 | N |  |  | Y | 0x8001 | 0x2105 | Y | 0x8001 | 0x2105 | N |  |  | Y | 0x8001 | 0x2105 | Y | 0x8001 | 0x2105 | N |  |  | Y | 0x8001 | 0x2105 | Y | 0x8001 | 0x2105
LLVD2 Enable | 0 | 0 | 1 | NA | 0x2103 | UINT16 | 0 | [NO=0]/[YES=1] | N | Y | Y | Y | Y | Y | N | N |  | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8001 | 0x2152 | N |  |  | Y | 0x8001 | 0x2152 | N |  |  | Y | 0x8001 | 0x2152 | N |  |  | Y | 0x8001 | 0x2152 | N |  |  | N |  |  | Y | 0x8001 | 0x2152 | N |  |  | Y | 0x8001 | 0x2152 | Y | 0x8001 | 0x2152 | N |  |  | Y | 0x8001 | 0x2152 | Y | 0x8001 | 0x2152 | N |  |  | Y | 0x8001 | 0x2152 | Y | 0x8001 | 0x2152
LLVD2 Voltage | 44 | 36 | 56 | V | 0x2104 | UINT16 | 1 |  | N | Y | Y | Y | Y | Y | N | N |  | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8001 | 0x2154 | N |  |  | Y | 0x8001 | 0x2154 | N |  |  | Y | 0x8001 | 0x2154 | N |  |  | Y | 0x8001 | 0x2154 | N |  |  | N |  |  | Y | 0x8001 | 0x2154 | N |  |  | Y | 0x8001 | 0x2154 | Y | 0x8001 | 0x2154 | N |  |  | Y | 0x8001 | 0x2154 | Y | 0x8001 | 0x2154 | N |  |  | Y | 0x8001 | 0x2154 | Y | 0x8001 | 0x2154
LLVD2 Connection Voltage | 51.5 | 37 | 58 | V | 0x2105 | UINT16 | 1 |  | N | Y | Y | Y | Y | Y | N | N |  | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8001 | 0x2155 | N |  |  | Y | 0x8001 | 0x2155 | N |  |  | Y | 0x8001 | 0x2155 | N |  |  | Y | 0x8001 | 0x2155 | N |  |  | N |  |  | Y | 0x8001 | 0x2155 | N |  |  | Y | 0x8001 | 0x2155 | Y | 0x8001 | 0x2155 | N |  |  | Y | 0x8001 | 0x2155 | Y | 0x8001 | 0x2155 | N |  |  | Y | 0x8001 | 0x2155 | Y | 0x8001 | 0x2155
AC Overvoltage Threshold | 280 | 60 | 300 | V | 0x2106 | UINT16 | 0 |  | Y | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x2109 | Y | 0x8001 | 0x20CC/0x21B5 | Y | 0x8001 | 0x20CC/0x21B5 | Y | 0x8231 | 0x2109/0x269E | Y | 0x8001 | 0x2109 | Y | 0x8001 | 0x20CC/0x21B5 | Y | 0x8001 | 0x20CC/0x21B5 | Y | 0x8231 | 0x2109/0x269E | N |  |  | Y | 0x8001 | 0x2109 | Y | 0x8001 | 0x20CC/0x21B5 | Y | 0x8001 | 0x20CC/0x21B5 | Y | 0x8001 | 0x20CC/0x21B5 | Y | 0x8001 | 0x20CC/0x21B5 | Y | 0x8001 | 0x2109 | Y | 0x8001 | 0x20CC/0x21B5 | Y | 0x8001 | 0x20CC/0x21B5 | Y | 0x8001 | 0x2109 | Y | 0x8001 | 0x20CC/0x21B5
AC Undervoltage Threshold | 180 | 60 | 300 | V | 0x2107 | UINT16 | 0 |  | Y | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x2110 | Y | 0x8001 | 0x20CD/0x21B6 | Y | 0x8001 | 0x20CD/0x21B6 | Y | 0x8231 | 0x2110/0x269F | Y | 0x8001 | 0x2110 | Y | 0x8001 | 0x20CD/0x21B6 | Y | 0x8001 | 0x20CD/0x21B6 | Y | 0x8231 | 0x2110/0x269F | N |  |  | Y | 0x8001 | 0x2110 | Y | 0x8001 | 0x20CD/0x21B6 | Y | 0x8001 | 0x20CD/0x21B6 | Y | 0x8001 | 0x20CD/0x21B6 | Y | 0x8001 | 0x20CD/0x21B6 | Y | 0x8001 | 0x2110 | Y | 0x8001 | 0x20CD/0x21B6 | Y | 0x8001 | 0x20CD/0x21B6 | Y | 0x8001 | 0x2110 | Y | 0x8001 | 0x20CD/0x21B6
DC Overvoltage Threshold | 58 | 53 | 60 | V | 0x2108 | UINT16 | 1 |  | Y | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x2111 | Y | 0x8001 | 0x20C8 | Y | 0x8001 | 0x20C8 | Y | 0x8231 | 0x2111 | Y | 0x8001 | 0x2111 | Y | 0x8001 | 0x20C8 | Y | 0x8001 | 0x20C8 | Y | 0x8231 | 0x2111 | Y | 0x8001 | 0x2111 | Y | 0x8001 | 0x2111 | Y | 0x8001 | 0x20C8 | Y | 0x8001 | 0x20C8 | Y | 0x8001 | 0x20C8 | Y | 0x8001 | 0x20C8 | Y | 0x8001 | 0x2111 | Y | 0x8001 | 0x20C8 | Y | 0x8001 | 0x20C8 | Y | 0x8001 | 0x2111 | Y | 0x8001 | 0x20C8
DC Undervoltage Threshold | 45 | 35 | 57 | V | 0x2109 | UINT16 | 1 |  | Y | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x2112 | Y | 0x8001 | 0x20C9 | Y | 0x8001 | 0x20C9 | Y | 0x8231 | 0x2112 | Y | 0x8001 | 0x2112 | Y | 0x8001 | 0x20C9 | Y | 0x8001 | 0x20C9 | Y | 0x8231 | 0x2112 | N |  |  | Y | 0x8001 | 0x2112 | Y | 0x8001 | 0x20C9 | Y | 0x8001 | 0x20C9 | Y | 0x8001 | 0x20C9 | Y | 0x8001 | 0x20C9 | Y | 0x8001 | 0x2112 | Y | 0x8001 | 0x20C9 | Y | 0x8001 | 0x20C9 | Y | 0x8001 | 0x2112 | Y | 0x8001 | 0x20C9
AC Overfrequency Alarm Threshold | 66 | 40 | 70 | Hz | 0x210A | UINT16 | 0 |  | Y | N | N | N | N | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y |  |  |  | Y | 0x8001 | 0x20CA | Y | 0x8001 | 0x20CA | Y | 0x8231 | 0x2A00 |  |  |  | Y | 0x8001 | 0x20CA | Y | 0x8001 | 0x20CA | Y | 0x8231 | 0x2A00 | N | [5 empty] | Y | 0x8001 | 0x20CA | Y | 0x8001 | 0x20CA | Y | 0x8001 | 0x20CA | Y | 0x8001 | 0x20CA |  |  |  | Y | 0x8001 | 0x20CA | Y | 0x8001 | 0x20CA |  |  |  | Y | 0x8001 | 0x20CA
AC Underfrequency Alarm Threshold | 45 | 40 | 70 | Hz | 0x210B | UINT16 | 0 |  | Y | N | N | N | N | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y |  |  |  | Y | 0x8001 | 0x20CB | Y | 0x8001 | 0x20CB | Y | 0x8231 | 0x2A01 |  |  |  | Y | 0x8001 | 0x20CB | Y | 0x8001 | 0x20CB | Y | 0x8231 | 0x2A01 | N | [5 empty] | Y | 0x8001 | 0x20CB | Y | 0x8001 | 0x20CB | Y | 0x8001 | 0x20CB | Y | 0x8001 | 0x20CB |  |  |  | Y | 0x8001 | 0x20CB | Y | 0x8001 | 0x20CB |  |  |  | Y | 0x8001 | 0x20CB
LLVD1 Disconnect Mode | 0 | 0 | 2 | NA | 0x210C | UINT16 | 0 | [Voltage Mode=0]/[Time Mode=1]/[Capacity Mode=2] | N | N | N | N | Y | Y | N | N | N | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x2103 | N |  |  | Y | 0x8001 | 0x2103 | Y | 0x8226 | 0x2103 | Y | 0x8001 | 0x2103 | N |  |  | Y | 0x8001 | 0x2103 | Y | 0x8226 | 0x2103 | N |  |  | Y | 0x8001 | 0x2103 | N |  |  | Y | 0x8001 | 0x2103 | Y | 0x8001 | 0x2103 | N |  |  | Y | 0x8001 | 0x2103 | Y | 0x8001 | 0x2103 | N |  |  | Y | 0x8001 | 0x2103 | Y | 0x8001 | 0x2103
LLVD1 Disconnect Time | 180 | 0 | 50000 | Min | 0x210D | UINT16 | 0 |  | N | N | N | N | Y | Y | N | N | N | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x2106 | N |  |  | Y | 0x8001 | 0x2106 | Y | 0x8226 | 0x2106 | Y | 0x8001 | 0x2106 | N |  |  | Y | 0x8001 | 0x2106 | Y | 0x8226 | 0x2106 | N |  |  | Y | 0x8001 | 0x2106 | N |  |  | Y | 0x8001 | 0x2106 | Y | 0x8001 | 0x2106 | N |  |  | Y | 0x8001 | 0x2106 | Y | 0x8001 | 0x2106 | N |  |  | Y | 0x8001 | 0x2106 | Y | 0x8001 | 0x2106
LLVD1 Disconnect Capacity | 25 | 0 | 99 | % | 0x210E | UINT16 | 1 |  | N | N | N | N | Y | Y | N | N | N | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x2107 | N |  |  | Y | 0x8001 | 0x2107 | Y | 0x8226 | 0x2107 | Y | 0x8001 | 0x2107 | N |  |  | Y | 0x8001 | 0x2107 | Y | 0x8226 | 0x2107 | N |  |  | Y | 0x8001 | 0x2107 | N |  |  | Y | 0x8001 | 0x2107 | Y | 0x8001 | 0x2107 | N |  |  | Y | 0x8001 | 0x2107 | Y | 0x8001 | 0x2107 | N |  |  | Y | 0x8001 | 0x2107 | Y | 0x8001 | 0x2107
LLVD1 High Temp Disconnect Enable | 0 | 0 | 1 | NA | 0x210F | UINT16 | 0 | [Disable=0]/[Enable=1] | N | N | N | N | Y | Y | N | N | N | Y | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8001 | 0x28C0 | Y | 0x8226 | 0x28C0 | N |  |  | N |  |  | Y | 0x8001 | 0x28C0 | Y | 0x8226 | 0x28C0 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28C0 | Y | 0x8001 | 0x28C0 | N |  |  | N |  |  | Y | 0x8001 | 0x28C0 | N |  |  | N |  |  | Y | 0x8001 | 0x28C0
LLVD1 High Temp Disconnect Temperature | 65 | 25 | 80 | degC | 0x2110 | UINT16 | 1 |  | N | N | N | N | Y | Y | N | N | N | Y | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8001 | 0x28C1 | Y | 0x8226 | 0x28C1 | N |  |  | N |  |  | Y | 0x8001 | 0x28C1 | Y | 0x8226 | 0x28C1 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28C1 | Y | 0x8001 | 0x28C1 | N |  |  | N |  |  | Y | 0x8001 | 0x28C1 | N |  |  | N |  |  | Y | 0x8001 | 0x28C1
LLVD2 Disconnect Mode | 0 | 0 | 2 | NA | 0x2111 | UINT16 | 0 | [Voltage Mode=0]/[Time Mode=1]/[Capacity Mode=2] | N | N | N | N | Y | Y | N | N | N | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8001 | 0x2153 | N |  |  | Y | 0x8001 | 0x2153 | N |  |  | Y | 0x8001 | 0x2153 | N |  |  | Y | 0x8001 | 0x2153 | N |  |  | N |  |  | Y | 0x8001 | 0x2153 | N |  |  | Y | 0x8001 | 0x2153 | Y | 0x8001 | 0x2153 | N |  |  | Y | 0x8001 | 0x2153 | Y | 0x8001 | 0x2153 | N |  |  | Y | 0x8001 | 0x2153 | Y | 0x8001 | 0x2153
LLVD2 Disconnect Time | 360 | 0 | 50000 | Min | 0x2112 | UINT16 | 0 |  | N | N | N | N | Y | Y | N | N | N | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8001 | 0x2156 | N |  |  | Y | 0x8001 | 0x2156 | N |  |  | Y | 0x8001 | 0x2156 | N |  |  | Y | 0x8001 | 0x2156 | N |  |  | N |  |  | Y | 0x8001 | 0x2156 | N |  |  | Y | 0x8001 | 0x2156 | Y | 0x8001 | 0x2156 | N |  |  | Y | 0x8001 | 0x2156 | Y | 0x8001 | 0x2156 | N |  |  | Y | 0x8001 | 0x2156 | Y | 0x8001 | 0x2156
LLVD2 Disconnect Capacity | 15 | 0 | 99 | % | 0x2113 | UINT16 | 1 |  | N | N | N | N | Y | Y | N | N | N | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8001 | 0x2157 | N |  |  | Y | 0x8001 | 0x2157 | N |  |  | Y | 0x8001 | 0x2157 | N |  |  | Y | 0x8001 | 0x2157 | N |  |  | N |  |  | Y | 0x8001 | 0x2157 | N |  |  | Y | 0x8001 | 0x2157 | Y | 0x8001 | 0x2157 | N |  |  | Y | 0x8001 | 0x2157 | Y | 0x8001 | 0x2157 | N |  |  | Y | 0x8001 | 0x2157 | Y | 0x8001 | 0x2157
LLVD2 High Temp Disconnect Enable | 0 | 0 | 1 | NA | 0x2114 | UINT16 | 0 | [Disable=0]/[Enable=1] | N | N | N | N | Y | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8001 | 0x28C3 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28C3 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28C3 | Y | 0x8001 | 0x28C3 | N |  |  | N |  |  | Y | 0x8001 | 0x28C3 | N |  |  | N |  |  | Y | 0x8001 | 0x28C3
LLVD2 High Temp Disconnect Temperature | 65 | 25 | 80 | degC | 0x2115 | UINT16 | 1 |  | N | N | N | N | Y | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8001 | 0x28C4 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28C4 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28C4 | Y | 0x8001 | 0x28C4 | N |  |  | N |  |  | Y | 0x8001 | 0x28C4 | N |  |  | N |  |  | Y | 0x8001 | 0x28C4
LLVD3 Enable | 1 | 0 | 1 | NA | 0x2116 | UINT16 | 0 | [NO=0]/[YES=1] | N | N | N | N | Y | Y | N | N | N | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8001 | 0x2767 | N |  |  | Y | 0x8001 | 0x2767 | N |  |  | Y | 0x8001 | 0x2767 | N |  |  | Y | 0x8001 | 0x2767 | N |  |  | N |  |  | Y | 0x8001 | 0x2767 | N |  |  | Y | 0x8001 | 0x2767 | Y | 0x8001 | 0x2767 | N |  |  | Y | 0x8001 | 0x2767 | Y | 0x8001 | 0x2767 | N |  |  | Y | 0x8001 | 0x2767 | Y | 0x8001 | 0x2767
LLVD3 Disconnect Voltage | 44 | 35 | 56 | V | 0x2117 | UINT16 | 1 | NA | N | N | N | N | Y | Y | N | N | N | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8001 | 0x2769 | N |  |  | Y | 0x8001 | 0x2769 | N |  |  | Y | 0x8001 | 0x2769 | N |  |  | Y | 0x8001 | 0x2769 | N |  |  | N |  |  | Y | 0x8001 | 0x2769 | N |  |  | Y | 0x8001 | 0x2769 | Y | 0x8001 | 0x2769 | N |  |  | Y | 0x8001 | 0x2769 | Y | 0x8001 | 0x2769 | N |  |  | Y | 0x8001 | 0x2769 | Y | 0x8001 | 0x2769
LLVD3 Connection Voltage | 51.5 | 37 | 58 | V | 0x2118 | UINT16 | 1 | NA | N | N | N | N | Y | Y | N | N | N | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8001 | 0x276A | N |  |  | Y | 0x8001 | 0x276A | N |  |  | Y | 0x8001 | 0x276A | N |  |  | Y | 0x8001 | 0x276A | N |  |  | N |  |  | Y | 0x8001 | 0x276A | N |  |  | Y | 0x8001 | 0x276A | Y | 0x8001 | 0x276A | N |  |  | Y | 0x8001 | 0x276A | Y | 0x8001 | 0x276A | N |  |  | Y | 0x8001 | 0x276A | Y | 0x8001 | 0x276A
LLVD3 Disconnect Mode | 0 | 0 | 2 | NA | 0x2119 | UINT16 | 0 | [Voltage Mode=0]/[Time Mode=1]/[Capacity Mode=2] | N | N | N | N | Y | Y | N | N | N | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8001 | 0x2768 | N |  |  | Y | 0x8001 | 0x2768 | N |  |  | Y | 0x8001 | 0x2768 | N |  |  | Y | 0x8001 | 0x2768 | N |  |  | N |  |  | Y | 0x8001 | 0x2768 | N |  |  | Y | 0x8001 | 0x2768 | Y | 0x8001 | 0x2768 | N |  |  | Y | 0x8001 | 0x2768 | Y | 0x8001 | 0x2768 | N |  |  | Y | 0x8001 | 0x2768 | Y | 0x8001 | 0x2768
LLVD3 Disconnect Time | 360 | 0 | 50000 | Min | 0x211A | UINT16 | 0 |  | N | N | N | N | Y | Y | N | N | N | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8001 | 0x276B | N |  |  | Y | 0x8001 | 0x276B | N |  |  | Y | 0x8001 | 0x276B | N |  |  | Y | 0x8001 | 0x276B | N |  |  | N |  |  | Y | 0x8001 | 0x276B | N |  |  | Y | 0x8001 | 0x276B | Y | 0x8001 | 0x276B | N |  |  | Y | 0x8001 | 0x276B | Y | 0x8001 | 0x276B | N |  |  | Y | 0x8001 | 0x276B | Y | 0x8001 | 0x276B
LLVD3 Disconnect Capacity | 15 | 0 | 99 | % | 0x211B | UINT16 | 1 |  | N | N | N | N | Y | Y | N | N | N | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8001 | 0x276C | N |  |  | Y | 0x8001 | 0x276C | N |  |  | Y | 0x8001 | 0x276C | N |  |  | Y | 0x8001 | 0x276C | N |  |  | N |  |  | Y | 0x8001 | 0x276C | N |  |  | Y | 0x8001 | 0x276C | Y | 0x8001 | 0x276C | N |  |  | Y | 0x8001 | 0x276C | Y | 0x8001 | 0x276C | N |  |  | Y | 0x8001 | 0x276C | Y | 0x8001 | 0x276C
LLVD3 High Temp Disconnect Enable | 0 | 0 | 1 | NA | 0x211C | UINT16 | 0 | [Disable=0]/[Enable=1] | N | N | N | N | Y | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8001 | 0x28C6 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28C6 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28C6 | Y | 0x8001 | 0x28C6 | N |  |  | N |  |  | Y | 0x8001 | 0x28C6 | N |  |  | N |  |  | Y | 0x8001 | 0x28C6
LLVD3 High Temp Disconnect Temperature | 65 | 25 | 80 | degC | 0x211D | UINT16 | 1 |  | N | N | N | N | Y | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8001 | 0x28C7 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28C7 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28C7 | Y | 0x8001 | 0x28C7 | N |  |  | N |  |  | Y | 0x8001 | 0x28C7 | N |  |  | N |  |  | Y | 0x8001 | 0x28C7
LLVD4 Enable | 1 | 0 | 1 | NA | 0x211E | UINT16 | 0 | [NO=0]/[YES=1] | N | N | N | N | Y | Y | N | N | N | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8001 | 0x2796 | N |  |  | Y | 0x8001 | 0x2796 | N |  |  | Y | 0x8001 | 0x2796 | N |  |  | Y | 0x8001 | 0x2796 | N |  |  | N |  |  | Y | 0x8001 | 0x2796 | N |  |  | Y | 0x8001 | 0x2796 | Y | 0x8001 | 0x2796 | N |  |  | Y | 0x8001 | 0x2796 | Y | 0x8001 | 0x2796 | N |  |  | Y | 0x8001 | 0x2796 | Y | 0x8001 | 0x2796
LLVD4 Disconnect Voltage | 44 | 35 | 56 | V | 0x211F | UINT16 | 1 | NA | N | N | N | N | Y | Y | N | N | N | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8001 | 0x2798 | N |  |  | Y | 0x8001 | 0x2798 | N |  |  | Y | 0x8001 | 0x2798 | N |  |  | Y | 0x8001 | 0x2798 | N |  |  | N |  |  | Y | 0x8001 | 0x2798 | N |  |  | Y | 0x8001 | 0x2798 | Y | 0x8001 | 0x2798 | N |  |  | Y | 0x8001 | 0x2798 | Y | 0x8001 | 0x2798 | N |  |  | Y | 0x8001 | 0x2798 | Y | 0x8001 | 0x2798
LLVD4 Connection Voltage | 51.5 | 37 | 58 | V | 0x2120 | UINT16 | 1 | NA | N | N | N | N | Y | Y | N | N | N | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8001 | 0x2799 | N |  |  | Y | 0x8001 | 0x2799 | N |  |  | Y | 0x8001 | 0x2799 | N |  |  | Y | 0x8001 | 0x2799 | N |  |  | N |  |  | Y | 0x8001 | 0x2799 | N |  |  | Y | 0x8001 | 0x2799 | Y | 0x8001 | 0x2799 | N |  |  | Y | 0x8001 | 0x2799 | Y | 0x8001 | 0x2799 | N |  |  | Y | 0x8001 | 0x2799 | Y | 0x8001 | 0x2799
LLVD4 Disconnect Mode | 0 | 0 | 2 | NA | 0x2121 | UINT16 | 0 | [Voltage Mode=0]/[Time Mode=1]/[Capacity Mode=2] | N | N | N | N | Y | Y | N | N | N | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8001 | 0x2797 | N |  |  | Y | 0x8001 | 0x2797 | N |  |  | Y | 0x8001 | 0x2797 | N |  |  | Y | 0x8001 | 0x2797 | N |  |  | N |  |  | Y | 0x8001 | 0x2797 | N |  |  | Y | 0x8001 | 0x2797 | Y | 0x8001 | 0x2797 | N |  |  | Y | 0x8001 | 0x2797 | Y | 0x8001 | 0x2797 | N |  |  | Y | 0x8001 | 0x2797 | Y | 0x8001 | 0x2797
LLVD4 Disconnect Time | 360 | 0 | 50000 | Min | 0x2122 | UINT16 | 0 |  | N | N | N | N | Y | Y | N | N | N | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8001 | 0x279A | N |  |  | Y | 0x8001 | 0x279A | N |  |  | Y | 0x8001 | 0x279A | N |  |  | Y | 0x8001 | 0x279A | N |  |  | N |  |  | Y | 0x8001 | 0x279A | N |  |  | Y | 0x8001 | 0x279A | Y | 0x8001 | 0x279A | N |  |  | Y | 0x8001 | 0x279A | Y | 0x8001 | 0x279A | N |  |  | Y | 0x8001 | 0x279A | Y | 0x8001 | 0x279A
LLVD4 Disconnect Capacity | 15 | 0 | 99 | % | 0x2123 | UINT16 | 1 |  | N | N | N | N | Y | Y | N | N | N | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8001 | 0x279B | N |  |  | Y | 0x8001 | 0x279B | N |  |  | Y | 0x8001 | 0x279B | N |  |  | Y | 0x8001 | 0x279B | N |  |  | N |  |  | Y | 0x8001 | 0x279B | N |  |  | Y | 0x8001 | 0x279B | Y | 0x8001 | 0x279B | N |  |  | Y | 0x8001 | 0x279B | Y | 0x8001 | 0x279B | N |  |  | Y | 0x8001 | 0x279B | Y | 0x8001 | 0x279B
LLVD4 High Temp Disconnect Enable | 0 | 0 | 1 | NA | 0x2124 | UINT16 | 0 | [Disable=0]/[Enable=1] | N | N | N | N | Y | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8001 | 0x28C9 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28C9 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28C9 | Y | 0x8001 | 0x28C9 | N |  |  | N |  |  | Y | 0x8001 | 0x28C9 | N |  |  | N |  |  | Y | 0x8001 | 0x28C9
LLVD4 High Temp Disconnect Temperature | 65 | 25 | 80 | degC | 0x2125 | UINT16 | 1 |  | N | N | N | N | Y | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8001 | 0x28CA | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28CA | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28CA | Y | 0x8001 | 0x28CA | N |  |  | N |  |  | Y | 0x8001 | 0x28CA | N |  |  | N |  |  | Y | 0x8001 | 0x28CA
AC Type | 1 | 0 | 3 | NA | 0x2126 | UINT16 | 0 | [Single Phase=0]/[Three Phases=1]/[Three Live Lines=2]/[D-Live Lines=3] | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
48V Side DC Input Type | 0 | 0 | 2 | NA | 0x2127 | UINT16 | 0 | [The Third Input=0]/[Acid Battery=1]/[Lithium Battery=2] | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Adjust DC Output Voltage | 53.5 | 43 | 58 | V | 0x2128 | UINT16 | 1 | For 5G Booster----The host can adjust the DC output voltage of 5G Booster System through the address and it adjusts the 48V side DC voltage. | N | N | N | N | N | N | N | Note: Inner signal, not open. |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
HW Power Connecting Enable | 0 | 0 | 1 | NA | 0x2129 | UINT16 | 0 | [NO=0]/[YES=1] | N | N | N | N | N | N | N | Note: Inner signal, not open. |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Only DC/DC Power | 0 | 0 | 1 | NA | 0x212A | UINT16 | 0 | [NO=0]/[YES=1] | N | N | N | N | N | N | N | Note: Inner signal, not open. |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AC Overvoltage Threshold | 280 | 60 | 300 | V | 0x212B | UINT16 | 0 | AC2 | N | N | N | N | N | Y | N | N | N | N | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8001 | 0x20CC/0x21B5 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20CC/0x21B5 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20CC/0x21B5 | Y | 0x8001 | 0x20CC/0x21B5 | N |  |  | N |  |  | Y | 0x8001 | 0x20CC/0x21B5 | N |  |  | N |  |  | Y | 0x8001 | 0x20CC/0x21B5
AC Undervoltage Threshold | 180 | 60 | 300 | V | 0x212C | UINT16 | 0 | AC2 | N | N | N | N | N | Y | N | N | N | N | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8001 | 0x20CD/0x21B6 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20CD/0x21B6 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20CD/0x21B6 | Y | 0x8001 | 0x20CD/0x21B6 | N |  |  | N |  |  | Y | 0x8001 | 0x20CD/0x21B6 | N |  |  | N |  |  | Y | 0x8001 | 0x20CD/0x21B6
AC Overfrequency Alarm Threshold | 40 | 66 | 70 | Hz | 0x212D | UINT16 | 0 | AC2 | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8001 | 0x20CA | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20CA | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20CA | Y | 0x8001 | 0x20CA | N |  |  | N |  |  | Y | 0x8001 | 0x20CA | N |  |  | N |  |  | Y | 0x8001 | 0x20CA
AC Underfrequency Alarm Threshold | 40 | 45 | 70 | Hz | 0x212E | UINT16 | 0 | AC2 | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8001 | 0x20CB | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20CB | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20CB | Y | 0x8001 | 0x20CB | N |  |  | N |  |  | Y | 0x8001 | 0x20CB | N |  |  | N |  |  | Y | 0x8001 | 0x20CB
LLVD5 Enable | 1 | 0 | 1 | NA | 0x2130 | UINT16 | 0 | [NO=0]/[YES=1] | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20E6 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20E6 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20E6 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20E6 | N |  |  | N |  |  | Y | 0x8001 | 0x20E6 | N
LLVD5 Disconnect Voltage | 44 | 35 | 56 | V | 0x2131 | UINT16 | 1 | NA | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20E8 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20E8 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20E8 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20E8 | N |  |  | N |  |  | Y | 0x8001 | 0x20E8 | N
LLVD5 Connection Voltage | 51.5 | 37 | 58 | V | 0x2132 | UINT16 | 1 | NA | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20E9 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20E9 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20E9 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20E9 | N |  |  | N |  |  | Y | 0x8001 | 0x20E9 | N
LLVD5 Disconnect Mode | 0 | 0 | 2 | NA | 0x2133 | UINT16 | 0 | [Voltage Mode=0]/[Time Mode=1]/[Capacity Mode=2] | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20E7 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20E7 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20E7 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20E7 | N |  |  | N |  |  | Y | 0x8001 | 0x20E7 | N
LLVD5 Disconnect Time | 360 | 0 | 50000 | Min | 0x2134 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20EA | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20EA | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20EA | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20EA | N |  |  | N |  |  | Y | 0x8001 | 0x20EA | N
LLVD5 Disconnect Capacity | 15 | 0 | 99 | % | 0x2135 | UINT16 | 1 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20EB | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20EB | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20EB | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20EB | N |  |  | N |  |  | Y | 0x8001 | 0x20EB | N
LLVD5 High Temp Disconnect Enable | 0 | 0 | 1 | NA | 0x2136 | UINT16 | 0 | [Disable=0]/[Enable=1] | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
LLVD5 High Temp Disconnect Temperature | 65 | 25 | 80 | degC | 0x2137 | UINT16 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
[5 empty] | Registers Reserved | [20 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
LLVD6 Enable | 1 | 0 | 1 | NA | 0x2140 | UINT16 | 0 | [NO=0]/[YES=1] | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20F1 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F1 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F1 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F1 | N |  |  | N |  |  | Y | 0x8001 | 0x20F1 | N
LLVD6 Disconnect Voltage | 44 | 35 | 56 | V | 0x2141 | UINT16 | 1 | NA | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20F3 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F3 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F3 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F3 | N |  |  | N |  |  | Y | 0x8001 | 0x20F3 | N
LLVD6 Connection Voltage | 51.5 | 37 | 58 | V | 0x2142 | UINT16 | 1 | NA | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20F4 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F4 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F4 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F4 | N |  |  | N |  |  | Y | 0x8001 | 0x20F4 | N
LLVD6 Disconnect Mode | 0 | 0 | 2 | NA | 0x2143 | UINT16 | 0 | [Voltage Mode=0]/[Time Mode=1]/[Capacity Mode=2] | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20F2 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F2 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F2 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F2 | N |  |  | N |  |  | Y | 0x8001 | 0x20F2 | N
LLVD6 Disconnect Time | 360 | 0 | 50000 | Min | 0x2144 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20F5 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F5 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F5 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F5 | N |  |  | N |  |  | Y | 0x8001 | 0x20F5 | N
LLVD6 Disconnect Capacity | 15 | 0 | 99 | % | 0x2145 | UINT16 | 1 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20F6 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F6 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F6 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F6 | N |  |  | N |  |  | Y | 0x8001 | 0x20F6 | N
LLVD6 High Temp Disconnect Enable | 0 | 0 | 1 | NA | 0x2146 | UINT16 | 0 | [Disable=0]/[Enable=1] | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
LLVD6 High Temp Disconnect Temperature | 65 | 25 | 80 | degC | 0x2147 | UINT16 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
[5 empty] | Registers Reserved | [20 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
LLVD7 Enable | 1 | 0 | 1 | NA | 0x2150 | UINT16 | 0 | [NO=0]/[YES=1] | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20FB | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20FB | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20FB | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20FB | N |  |  | N |  |  | Y | 0x8001 | 0x20FB | N
LLVD7 Disconnect Voltage | 44 | 35 | 56 | V | 0x2151 | UINT16 | 1 | NA | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20FD | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20FD | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20FD | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20FD | N |  |  | N |  |  | Y | 0x8001 | 0x20FD | N
LLVD7 Connection Voltage | 51.5 | 37 | 58 | V | 0x2152 | UINT16 | 1 | NA | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20FE | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20FE | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20FE | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20FE | N |  |  | N |  |  | Y | 0x8001 | 0x20FE | N
LLVD7 Disconnect Mode | 0 | 0 | 2 | NA | 0x2153 | UINT16 | 0 | [Voltage Mode=0]/[Time Mode=1]/[Capacity Mode=2] | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20FC | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20FC | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20FC | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20FC | N |  |  | N |  |  | Y | 0x8001 | 0x20FC | N
LLVD7 Disconnect Time | 360 | 0 | 50000 | Min | 0x2154 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20FF | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20FF | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20FF | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20FF | N |  |  | N |  |  | Y | 0x8001 | 0x20FF | N
LLVD7 Disconnect Capacity | 15 | 0 | 99 | % | 0x2155 | UINT16 | 1 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x210A | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x210A | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x210A | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x210A | N |  |  | N |  |  | Y | 0x8001 | 0x210A | N
LLVD7 High Temp Disconnect Enable | 0 | 0 | 1 | NA | 0x2156 | UINT16 | 0 | [Disable=0]/[Enable=1] | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
LLVD7 High Temp Disconnect Temperature | 65 | 25 | 80 | degC | 0x2157 | UINT16 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
[5 empty] | Registers Reserved | [20 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
LLVD1 Plan Disconnect Enable | 0 | 0 | 1 | NA | 0x2160 | UINT16 | 0 | [Disable=0]/[Enable=1] | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x23A3 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x23A3 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x23A3 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x23A3 | N |  |  | N |  |  | Y | 0x8001 | 0x23A3 | N
LLVD1 Plan Disconnect Time | 23:00 | 0:00 | 23:59 | NA | 0x2161 | UINT16 | 0 | HH:MM, e.g. 23 00, means 23:00 | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x23A4 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x23A4 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x23A4 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x23A4 | N |  |  | N |  |  | Y | 0x8001 | 0x23A4 | N
LLVD1 Plan Disconnect Duration | 480 | 1 | 1440 | Min | 0x2162 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x23A5 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x23A5 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x23A5 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x23A5 | N |  |  | N |  |  | Y | 0x8001 | 0x23A5 | N
LLVD2 Plan Disconnect Enable | 0 | 0 | 1 | NA | 0x2163 | UINT16 | 0 | [Disable=0]/[Enable=1] | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x28AE | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28AE | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28AE | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28AE | N |  |  | N |  |  | Y | 0x8001 | 0x28AE | N
LLVD2 Plan Disconnect Time | 23:00 | 0:00 | 23:59 | NA | 0x2164 | UINT16 | 0 | HH:MM, e.g. 23 00, means 23:00 | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x28B0 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28B0 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28B0 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28B0 | N |  |  | N |  |  | Y | 0x8001 | 0x28B0 | N
LLVD2 Plan Disconnect Duration | 480 | 1 | 1440 | Min | 0x2165 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x28B2 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28B2 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28B2 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28B2 | N |  |  | N |  |  | Y | 0x8001 | 0x28B2 | N
LLVD3 Plan Disconnect Enable | 0 | 0 | 1 | NA | 0x2166 | UINT16 | 0 | [Disable=0]/[Enable=1] | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x28B4 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28B4 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28B4 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28B4 | N |  |  | N |  |  | Y | 0x8001 | 0x28B4 | N
LLVD3 Plan Disconnect Time | 23:00 | 0:00 | 23:59 | NA | 0x2167 | UINT16 | 0 | HH:MM, e.g. 23 00, means 23:00 | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x28B6 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28B6 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28B6 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28B6 | N |  |  | N |  |  | Y | 0x8001 | 0x28B6 | N
LLVD3 Plan Disconnect Duration | 480 | 1 | 1440 | Min | 0x2168 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x28B8 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28B8 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28B8 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28B8 | N |  |  | N |  |  | Y | 0x8001 | 0x28B8 | N
LLVD4 Plan Disconnect Enable | 0 | 0 | 1 | NA | 0x2169 | UINT16 | 0 | [Disable=0]/[Enable=1] | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x28BA | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28BA | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28BA | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28BA | N |  |  | N |  |  | Y | 0x8001 | 0x28BA | N
LLVD4 Plan Disconnect Time | 23:00 | 0:00 | 23:59 | NA | 0x216A | UINT16 | 0 | HH:MM, e.g. 23 00, means 23:00 | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x28BC | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28BC | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28BC | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28BC | N |  |  | N |  |  | Y | 0x8001 | 0x28BC | N
LLVD4 Plan Disconnect Duration | 480 | 1 | 1440 | Min | 0x216B | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x28BE | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28BE | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28BE | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x28BE | N |  |  | N |  |  | Y | 0x8001 | 0x28BE | N
LLVD5 Plan Disconnect Enable | 0 | 0 | 1 | NA | 0x216C | UINT16 | 0 | [Disable=0]/[Enable=1] | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20EC | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20EC | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20EC | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20EC | N |  |  | N |  |  | Y | 0x8001 | 0x20EC | N
LLVD5 Plan Disconnect Time | 23:00 | 0:00 | 23:59 | NA | 0x216D | UINT16 | 0 | HH:MM, e.g. 23 00, means 23:00 | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20ED | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20ED | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20ED | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20ED | N |  |  | N |  |  | Y | 0x8001 | 0x20ED | N
LLVD5 Plan Disconnect Duration | 480 | 1 | 1440 | Min | 0x216E | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20EE | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20EE | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20EE | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20EE | N |  |  | N |  |  | Y | 0x8001 | 0x20EE | N
LLVD6 Plan Disconnect Enable | 0 | 0 | 1 | NA | 0x216F | UINT16 | 0 | [Disable=0]/[Enable=1] | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20F7 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F7 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F7 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F7 | N |  |  | N |  |  | Y | 0x8001 | 0x20F7 | N
LLVD6 Plan Disconnect Time | 23:00 | 0:00 | 23:59 | NA | 0x2170 | UINT16 | 0 | HH:MM, e.g. 23 00, means 23:00 | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20F8 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F8 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F8 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F8 | N |  |  | N |  |  | Y | 0x8001 | 0x20F8 | N
LLVD6 Plan Disconnect Duration | 480 | 1 | 1440 | Min | 0x2171 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20F9 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F9 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F9 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20F9 | N |  |  | N |  |  | Y | 0x8001 | 0x20F9 | N
LLVD7 Plan Disconnect Enable | 0 | 0 | 1 | NA | 0x2172 | UINT16 | 0 | [Disable=0]/[Enable=1] | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x210B | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x210B | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x210B | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x210B | N |  |  | N |  |  | Y | 0x8001 | 0x210B | N
LLVD7 Plan Disconnect Time | 23:00 | 0:00 | 23:59 | NA | 0x2173 | UINT16 | 0 | HH:MM, e.g. 23 00, means 23:00 | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x210C | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x210C | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x210C | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x210C | N |  |  | N |  |  | Y | 0x8001 | 0x210C | N
LLVD7 Plan Disconnect Duration | 480 | 1 | 1440 | Min | 0x2174 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x210D | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x210D | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x210D | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x210D | N |  |  | N |  |  | Y | 0x8001 | 0x210D | N
LLVD1 Manual Control of Delayed Power-on Time | 0 | 0 | 7200 | s | 0x2175 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x2127 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2127 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2127 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2127 | N |  |  | N |  |  | Y | 0x8001 | 0x2127 | N
LLVD2 Manual Control of Delayed Power-on Time | 0 | 0 | 7200 | s | 0x2176 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x2128 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2128 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2128 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2128 | N |  |  | N |  |  | Y | 0x8001 | 0x2128 | N
LLVD3 Manual Control of Delayed Power-on Time | 0 | 0 | 7200 | s | 0x2177 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x212A | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x212A | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x212A | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x212A | N |  |  | N |  |  | Y | 0x8001 | 0x212A | N
LLVD4 Manual Control of Delayed Power-on Time | 0 | 0 | 7200 | s | 0x2178 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x212B | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x212B | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x212B | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x212B | N |  |  | N |  |  | Y | 0x8001 | 0x212B | N
LLVD5 Manual Control of Delayed Power-on Time | 0 | 0 | 7200 | s | 0x2179 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x212C | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x212C | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x212C | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x212C | N |  |  | N |  |  | Y | 0x8001 | 0x212C | N
LLVD6 Manual Control of Delayed Power-on Time | 0 | 0 | 7200 | s | 0x217A | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x212D | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x212D | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x212D | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x212D | N |  |  | N |  |  | Y | 0x8001 | 0x212D | N
LLVD7 Manual Control of Delayed Power-on Time | 0 | 0 | 7200 | s | 0x217B | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x212E | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x212E | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x212E | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x212E | N |  |  | N |  |  | Y | 0x8001 | 0x212E | N
LLVD1 Enable | 1 | 0 | 1 | NA | 0x217C | UINT16 | 0 | [NO=0]/[YES=1] | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
LLVD1 Disconnect Mode | 0 | 0 | 2 | NA | 0x217D | UINT16 | 0 | [Voltage Mode=0]/[Time Mode=1]/[Capacity Mode=2] | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
LLVD1 Voltage | 45 | 36 | 56 | V | 0x217E | UINT16 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
LLVD1 Connection Voltage | 51.5 | 37 | 58 | V | 0x217F | UINT16 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
LLVD1 Disconnect Time | 360 | 0 | 1000 | Min | 0x2180 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
LLVD1 Disconnect Capacity | 25 | 0 | 99 | % | 0x2181 | UINT16 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
LLVD1 Plan Disconnect Enable | 0 | 0 | 1 | NA | 0x2182 | UINT16 | 0 | [Disable=0]/[Enable=1] | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
LLVD1 Plan Disconnect Time | 0.95833 | 0 | 0.99931 | NA | 0x2183 | UINT16 | 0 | HH:MM, e.g. 23 00, means 23:00 | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
LLVD1 Plan Disconnect Duration | 480 | 1 | 1440 | Min | 0x2184 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
[5 empty] | Registers Reserved | [20 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Carrier Operator | 1 | 0 | 1 | NA | 0x2200 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Access Point Name |  |  |  | NA | 0x2201 | STRING | 0 | for 14 registers | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
[5 empty] | Registers Reserved | [20 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Access Point Number |  |  |  | NA | 0x2211 | STRING | 0 | for 14 registers | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
[5 empty] | Registers Reserved | [20 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
User Name |  |  |  | NA | 0x2221 | STRING | 0 | for 14 registers | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
[5 empty] | Registers Reserved | [20 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
User Password |  |  |  | NA | 0x2231 | STRING | 0 | for 14 registers | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
[5 empty] | Registers Reserved | [20 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
User Password | 0xC0A8000A | 0 | 4294967295 | NA | 0x2241 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
NetEco Backup Server IP Address | 0xC0A8000A | 0 | 4294967295 | NA | 0x2242 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
NetEco Port Number | 31220 | 1 | 65535 | NA | 0x2243 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
IP Address | 0xC0A8000A | 0 | 4294967295 | NA | 0x2244 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Subnet Mask | 0xFFFFFF00 | 0 | 4294967295 | NA | 0x2245 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Default Gateway | 0xC0A80001 | 0 | 4294967295 | NA | 0x2246 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
[5 empty] | Registers Reserved | [20 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Door Sensor | 0 | 0 | 1 | NA | 0x2251 | UINT16 | [NO=0]/[YES=1] |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x9031 | 0x2026 | Y | 0x9031 | 0x2026 | N |  |  | N |  |  | Y | 0x9031 | 0x2026 | Y | 0x9031 | 0x2026 | N |  |  | N |  |  | N |  |  | Y | 0x9031 | 0x2026 | Y | 0x9031 | 0x2026 | Y | 0x9031 | 0x2026 | Y | 0x9031 | 0x2026 | N |  |  | Y | 0x9031 | 0x2026 | Y | 0x9031 | 0x2026 | N |  |  | Y | 0x9031 | 0x2026
[5 empty] | Registers Reserved | [20 empty] | N |  | N | [8 empty] | N |  |  | N | [8 empty] | N |  |  | N |  |  | N | [14 empty] | N | [8 empty] | N
Battery Rated Capacity | 100 | 5 | 10000 | Ah | 0x2300 | UINT16 | 0 |  | Y | Y | Y | Y | Y | Y | N | Y |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x2002 | Y | 0x8004 | 0x2002 | N |  |  | N |  |  | Y | 0x8004 | 0x2002 | Y | 0x8004 | 0x2002 | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x2002 | Y | 0x8004 | 0x2002 | N |  |  | N |  |  | Y | 0x8004 | 0x2002 | N |  |  | N |  |  | Y | 0x8004 | 0x2002
Float Charging Voltage | 53.5 | 42 | 58 | V | 0x2301 | UINT16 | 1 |  | Y | Y | Y | Y | Y | Y | N | Y |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x2007 | Y | 0x8004 | 0x2007 | N |  |  | N |  |  | Y | 0x8004 | 0x2007 | Y | 0x8004 | 0x2007 | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x2007 | Y | 0x8004 | 0x2007 | N |  |  | N |  |  | Y | 0x8004 | 0x2007 | N |  |  | N |  |  | Y | 0x8004 | 0x2007
Boost Charging Voltage | 56.4 | 42 | 58 | V | 0x2302 | UINT16 | 1 |  | Y | Y | Y | Y | Y | Y | N | Y |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x2006 | Y | 0x8004 | 0x2006 | N |  |  | N |  |  | Y | 0x8004 | 0x2006 | Y | 0x8004 | 0x2006 | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x2006 | Y | 0x8004 | 0x2006 | N |  |  | N |  |  | Y | 0x8004 | 0x2006 | N |  |  | N |  |  | Y | 0x8004 | 0x2006
BLVD Enable | 1 | 0 | 1 | NA | 0x2303 | UINT16 | 0 | [NO=0]/[YES=1] | Y | Y | Y | Y | Y | Y | N | Y |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x202E | Y | 0x8004 | 0x202E | N |  |  | N |  |  | Y | 0x8004 | 0x202E | Y | 0x8004 | 0x202E | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x202E | Y | 0x8004 | 0x202E | N |  |  | N |  |  | Y | 0x8004 | 0x202E | N |  |  | N |  |  | Y | 0x8004 | 0x202E
BLVD Voltage | 43.2 | 36 | 56 | V | 0x2304 | UINT16 | 1 |  | Y | Y | Y | Y | Y | Y | N | Y |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x2030 | Y | 0x8004 | 0x2030 | N |  |  | N |  |  | Y | 0x8004 | 0x2030 | Y | 0x8004 | 0x2030 | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x2030 | Y | 0x8004 | 0x2030 | N |  |  | N |  |  | Y | 0x8004 | 0x2030 | N |  |  | N |  |  | Y | 0x8004 | 0x2030
BLVD Connection Voltage | 51.5 | 37 | 58 | V | 0x2305 | UINT16 | 1 |  | Y | Y | Y | Y | Y | Y | N | Y |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x2036 | Y | 0x8004 | 0x2036 | N |  |  | N |  |  | Y | 0x8004 | 0x2036 | Y | 0x8004 | 0x2036 | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x2036 | Y | 0x8004 | 0x2036 | N |  |  | N |  |  | Y | 0x8004 | 0x2036 | N |  |  | N |  |  | Y | 0x8004 | 0x2036
Charge Current Limit Coefficient | 0.15 | 0.05 | 0.25 | NA | 0x2306 | UINT16 | 2 |  | Y | Y | Y | Y | Y | Y | N | Y |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x200A | Y | 0x8004 | 0x200A | N |  |  | N |  |  | Y | 0x8004 | 0x200A | Y | 0x8004 | 0x200A | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x200A | Y | 0x8004 | 0x200A | N |  |  | N |  |  | Y | 0x8004 | 0x200A | N |  |  | N |  |  | Y | 0x8004 | 0x200A
BLVD Disconnect Mode | 0 | 0 | 2 | NA | 0x2307 | UINT16 | 0 | [Voltage Mode=0]/[Time Mode=1]/[Capacity Mode=2] | N | N | N | N | Y | Y | N | Y |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x202F | Y | 0x8004 | 0x202F | N |  |  | N |  |  | Y | 0x8004 | 0x202F | Y | 0x8004 | 0x202F | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x202F | Y | 0x8004 | 0x202F | N |  |  | N |  |  | Y | 0x8004 | 0x202F | N |  |  | N |  |  | Y | 0x8004 | 0x202F
BLVD Disconnect Time | 480 | 0 | 10000 | Min | 0x2308 | UINT16 | 0 |  | N | N | N | N | Y | Y | N | Y |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x2031 | Y | 0x8004 | 0x2031 | N |  |  | N |  |  | Y | 0x8004 | 0x2031 | Y | 0x8004 | 0x2031 | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x2031 | Y | 0x8004 | 0x2031 | N |  |  | N |  |  | Y | 0x8004 | 0x2031 | N |  |  | N |  |  | Y | 0x8004 | 0x2031
BLVD Disconnect Capacity | 5 | 0 | 99 | % | 0x2309 | UINT16 | 1 |  | N | N | N | N | Y | Y | N | Y |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x2035 | Y | 0x8004 | 0x2035 | N |  |  | N |  |  | Y | 0x8004 | 0x2035 | Y | 0x8004 | 0x2035 | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x2035 | Y | 0x8004 | 0x2035 | N |  |  | N |  |  | Y | 0x8004 | 0x2035 | N |  |  | N |  |  | Y | 0x8004 | 0x2035
[5 empty] | Registers Reserved | [10 empty] | N | [9 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
DC Ultra Low Voltage | 44 | 35 | 57 | V | 0x23F0 | UINT16 | 1 | [7 empty] | N | N |  | N |  |  |  | Y |  |  | Y | N | Y | N |  |  | Y | 0x8226 | 0x2114 | Y | 0x8226 | 0x2114 | N |  |  | N |  |  | Y | 0x8226 | 0x2114 | Y | 0x8226 | 0x2114 | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x2114 | Y | 0x8226 | 0x2114 | Y | 0x8226 | 0x2114 | Y | 0x8226 | 0x2114 | N |  |  | Y | 0x8226 | 0x2114 | Y | 0x8226 | 0x2114 | N |  |  | Y | 0x8226 | 0x2114
DC Ultra High Voltage | 59 | 53 | 60 | V | 0x23F1 | UINT16 | 1 | [7 empty] | N | N |  | N |  |  |  | Y |  |  | Y | N | Y | N |  |  | Y | 0x8226 | 0x2113 | Y | 0x8226 | 0x2113 | N |  |  | N |  |  | Y | 0x8226 | 0x2113 | Y | 0x8226 | 0x2113 | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x2113 | Y | 0x8226 | 0x2113 | Y | 0x8226 | 0x2113 | Y | 0x8226 | 0x2113 | N |  |  | Y | 0x8226 | 0x2113 | Y | 0x8226 | 0x2113 | N |  |  | Y | 0x8226 | 0x2113
[5 empty] | Registers Reserved | [10 empty] | N | [9 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Air Conditioner 1 Work Temperature | 45 | 35 | 50 | degC | 0x2400 | INT16 | 1 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x800B | 0x2224/0x2233 | N |  |  | N |  |  | N |  |  | Y | 0x800B | 0x2224/0x2233 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x800B | 0x2224/0x2233 | Y | 0x800B | 0x2224/0x2233 | N |  |  | N |  |  | Y | 0x800B | 0x2224/0x2233 | N |  |  | N |  |  | Y | 0x800B | 0x2224/0x2233
Air Conditioner 1 Stop Temperature | 37 | 27 | 45 | degC | 0x2401 | INT16 | 1 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x800B | 0x2225/0x2234 | N |  |  | N |  |  | N |  |  | Y | 0x800B | 0x2225/0x2234 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x800B | 0x2225/0x2234 | Y | 0x800B | 0x2225/0x2234 | N |  |  | N |  |  | Y | 0x800B | 0x2225/0x2234 | N |  |  | N |  |  | Y | 0x800B | 0x2225/0x2234
[5 empty] | Registers Reserved | [20 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Air Conditioner 2 Work Temperature | 45 | 35 | 50 | degC | 0x2500 | INT16 | 1 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x2011/0x2013 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2011/0x2013 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2011/0x2013 | Y | 0x8022 | 0x2011/0x2013 | N |  |  | N |  |  | Y | 0x8022 | 0x2011/0x2013 | N |  |  | N |  |  | Y | 0x8022 | 0x2011/0x2013
Air Conditioner 2 Stop Temperature | 37 | 27 | 45 | degC | 0x2501 | INT16 | 1 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x2012/0x2014 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2012/0x2014 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2012/0x2014 | Y | 0x8022 | 0x2012/0x2014 | N |  |  | N |  |  | Y | 0x8022 | 0x2012/0x2014 | N |  |  | N |  |  | Y | 0x8022 | 0x2012/0x2014
[5 empty] | Registers(0x2502~0x251F) Reserved for the Air conditioner 2 |  |  |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
[5 empty] | Registers Reserved | [20 empty] | N |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Intelligent Air Conditioner Work Temperature | 45 | 38 | 50 | degC | 0x2600 | INT16 | 1 |  | N | N | N | N | Y | Y | N | N |  | Y |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8009 | 0x2029 | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x2029 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x2029 | Y | 0x8009 | 0x2029 | N |  |  | N |  |  | Y | 0x8009 | 0x2029 | N |  |  | N |  |  | Y | 0x8009 | 0x2029
Intelligent Air Conditioner Stop Temperature | 37 | 33 | 45 | degC | 0x2601 | INT16 | 1 |  | N | N | N | N | Y | Y | N | N |  | Y |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8009 | 0x202A | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x202A | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x202A | Y | 0x8009 | 0x202A | N |  |  | N |  |  | Y | 0x8009 | 0x202A | N |  |  | N |  |  | Y | 0x8009 | 0x202A
[5 empty] | Registers(0x2602~0x269F) Reserved for the smart aircondition |  |  |  | N | Y | Y | Y | Y | Y | N | N |  |  |  | N |  | Y | N |  | Y | N | Y | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
A/C Air Conditioner Work Temperature | 45 | 38 | 50 | degC | 0x26A0 | INT16 | 1 |  | N | N | N | N | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8021 | 0x2029 | N |  |  | N |  |  | N |  |  | Y | 0x8021 | 0x2029 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8021 | 0x2029 | Y | 0x8021 | 0x2029 | N |  |  | N |  |  | Y | 0x8021 | 0x2029 | N |  |  | N |  |  | Y | 0x8021 | 0x2029
A/C Air Conditioner Stop Temperature | 37 | 33 | 45 | degC | 0x26A1 | INT16 | 1 |  | N | N | N | N | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8021 | 0x202A | N |  |  | N |  |  | N |  |  | Y | 0x8021 | 0x202A | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8021 | 0x202A | Y | 0x8021 | 0x202A | N |  |  | N |  |  | Y | 0x8021 | 0x202A | N |  |  | N |  |  | Y | 0x8021 | 0x202A
[5 empty] | Registers(0x26A2~0x26A9) Reserved for the A/C aircondition |  |  |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Battery Charging Current Limit in combined cabinet N# N: 1–8 | 12 | 0 | 65535 | % | 0x26AA+(N-1)*16 | UINT16 | 0 |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Equalized Charge Voltage in combined cabinet N# N: 1–8 | 53.5 | 0 | 65535 | V | 0x26AB+(N-1)*16 | UINT16 | 1 |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Float Charge Voltage in combined cabinet N# N: 1–8 | 56.4 | 0 | 65535 | V | 0x26AC+(N-1)*16 | UINT16 | 1 |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
LLVD General Disconnect in combined cabinet N# N: 1–8 | 0 | 0 | 255 | NA | 0x26AD+(N-1)*16 | UINT16 | 0 | [Enable=1]/[Disable=0] | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
LLVD Disconnect Voltage in combined cabinet N# N: 1–8 | 44 | 35 | 53 | V | 0x26AE+(N-1)*16 | UINT16 | 1 |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
BLVD General Disconnect in combined cabinet N# N: 1–8 | 0 | 0 | 255 | NA | 0x26AF+(N-1)*16 | UINT16 | 0 | [Enable=1]/[Disable=0] | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
BLVD Disconnect Voltage in combined cabinet N# N: 1–8 | 43 | 35 | 56 | V | 0x27B0+(N-1)*16 | UINT16 | 1 |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Battery1 Capacity in combined cabinet N# N: 1–8 | 400 | 0 | 65535 | Ah | 0x27B1+(N-1)*16 | UINT16 | 0 |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Battery2 Capacity in combined cabinet N# N: 1–8 | 400 | 0 | 65535 | Ah | 0x27B2+(N-1)*16 | UINT16 | 0 |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bus Bar Overvoltage Threshold in combined cabinet N# N: 1–8 | 58.5 | 57 | 60 | V | 0x27B3+(N-1)*16 | UINT16 | 1 |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bus Bar Undervoltage Threshold in combined cabinet N# N: 1–8 | 46 | 35 | 56 | V | 0x27B4+(N-1)*16 | UINT16 | 1 |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AC Overvoltage Threshold in combined cabinet N# N: 1–8 | 280 | 60 | 600 | V | 0x27B5+(N-1)*16 | UINT16 | 1 |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AC Undervoltage Threshold in combined cabinet N# N: 1–8 | 180 | 60 | 600 | V | 0x27B6+(N-1)*16 | UINT16 | 1 |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Temperature Compensation Coefficient in combined cabinet N# N: 1–8 | 80 | 0 | 500 | mV/degC | 0x27B7+(N-1)*16 | UINT16 | 0 |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
[5 empty] | Reserve two registers for each cabinet. | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
[5 empty] | Registers Reserved(0x282A~0x282F) | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU1 Enable | 1 | 0 | 1 | NA | 0x2830 | UINT16 | 0 | [NO=0]/[YES=1] | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU1 Disconnect Voltage | 44 | 36 | 56 | V | 0x2831 | UINT16 | 1 | NA | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU1 Connection Voltage | 51.5 | 37 | 58 | V | 0x2832 | UINT16 | 1 | NA | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU1 Disconnect Mode | 0 | 0 | 2 | NA | 0x2833 | UINT16 | 0 | [Voltage Mode=0]/[Time Mode=1]/[Capacity Mode=2] | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU1 Disconnect Time | 360 | 0 | 50000 | Min | 0x2834 | UINT16 | 0 |  | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU1 Disconnect Capacity | 15 | 0 | 99 | % | 0x2835 | UINT16 | 1 |  | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU1 OutPut Voltage | 57 | 57 | 60 | V | 0x2836 | UINT16 | 1 | [8 empty] | Y | [9 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
[5 empty] | Reserve registers(0x2837) | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU2 Enable | 1 | 0 | 1 | NA | 0x2838 | UINT16 | 0 | [NO=0]/[YES=1] | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU2 Disconnect Voltage | 44 | 36 | 56 | V | 0x2839 | UINT16 | 1 | NA | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU2 Connection Voltage | 51.5 | 37 | 58 | V | 0x283A | UINT16 | 1 | NA | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU2 Disconnect Mode | 0 | 0 | 2 | NA | 0x283B | UINT16 | 0 | [Voltage Mode=0]/[Time Mode=1]/[Capacity Mode=2] | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU2 Disconnect Time | 360 | 0 | 50000 | Min | 0x283C | UINT16 | 0 |  | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU2 Disconnect Capacity | 15 | 0 | 99 | % | 0x283D | UINT16 | 1 |  | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU2 OutPut Voltage | 57 | 57 | 60 | V | 0x283E | UINT16 | 1 | [8 empty] | Y | [9 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
[5 empty] | Reserve registers(0x283F) | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU3 Enable | 1 | 0 | 1 | NA | 0x2840 | UINT16 | 0 | [NO=0]/[YES=1] | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU3 Disconnect Voltage | 44 | 36 | 56 | V | 0x2841 | UINT16 | 1 | NA | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU3 Connection Voltage | 51.5 | 37 | 58 | V | 0x2842 | UINT16 | 1 | NA | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU3 Disconnect Mode | 0 | 0 | 2 | NA | 0x2843 | UINT16 | 0 | [Voltage Mode=0]/[Time Mode=1]/[Capacity Mode=2] | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU3 Disconnect Time | 360 | 0 | 50000 | Min | 0x2844 | UINT16 | 0 |  | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU3 Disconnect Capacity | 15 | 0 | 99 | % | 0x2845 | UINT16 | 1 |  | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU3 OutPut Voltage | 57 | 57 | 60 | V | 0x2846 | UINT16 | 1 | [8 empty] | Y | [9 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
[5 empty] | Reserve two registers(0x2847) | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
[5 empty] | Register Reserved(0x2848~0x28FF) | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Number of ACB Cabinets | 1 | 1 | 10 | NA | 0x2900 | UINT16 | 0 | 16 in maximum, for DPS, its value always is 1. | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8018 | 0x2129 | N |  |  | N |  |  | N |  |  | Y | 0x8018 | 0x2129 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8018 | 0x2129 | Y | 0x8018 | 0x2129 | N |  |  | N |  |  | Y | 0x8018 | 0x2129 | N |  |  | N |  |  | Y | 0x8018 | 0x2129
[5 empty] | Register Reserved(0x2900~0x29FF) | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Input Over Voltage Percentage N:1-4 | 0 | 0 | 2 | NA | 0x2A00+(N-1)*4 | UINT16 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Input Under Voltage Percentage N:1-4 | 0 | 0 | 2 | NA | 0x2A01+(N-1)*4 | UINT16 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Frequency Change Alarm Threshold N:1-4 | 4 | 1 | 6 | Hz | 0x2A02+(N-1)*4 | UINT16 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
[5 empty] | Register Reserved(0x2A03) | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Output Voltage Level N:1-4 | 5 | 3 | 7 | NA | 0x2A10+(N-1)*8 | UINT16 | 0 | [200 V = 3][208 V = 4]/[220 V = 5]/[230 V = 6]/[240 V = 7] |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Output Freqency N:1-4 | 0 | 0 | 1 | NA | 0x2A11+(N-1)*8 | UINT16 | 0 | [50 Hz = 0]/[60 Hz = 1] |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Output Mode N:1-4 | 1 | 0 | 1 | NA | 0x2A12+(N-1)*8 | UINT16 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Upper Input Protection Voltage N:1-4 | 60 | 56 | 60 | V | 0x2A13+(N-1)*8 | UINT16 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Lower Input Protection Voltage N:1-4 | 41 | 41 | 48 | V | 0x2A14+(N-1)*8 | UINT16 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Upper Output Protection Voltage N:1-4 | 122 | 110 | 135 | % | 0x2A15+(N-1)*8 | UINT16 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Lower Output Protection Voltage N:1-4 | 83 | 65 | 90 | % | 0x2A16+(N-1)*8 | UINT16 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Upper Input Hysteresis Voltage N:1-4 | 5 | 3 | 5 | V | 0x2A17+(N-1)*8 | UINT16 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
[5 empty] | Register Reserved(none) | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load Setting Mode N:1-32 | 0 | 0 | 1 | NA | 0x2A30+(N-1)*32 | UINT16 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load Disconnect Mode N:1-32 | 0 | 0 | 1 | NA | 0x2A31+(N-1)*32 | UINT16 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load Disconnect Enabled N:1-32 | 1 | 0 | 1 | NA | 0x2A32+(N-1)*32 | UINT16 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load1 Disconnect Enabled N:1-32 | 1 | 0 | 1 | NA | 0x2A33+(N-1)*32 | UINT16 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load2 Disconnect Enabled N:1-32 | 1 | 0 | 1 | NA | 0x2A34+(N-1)*32 | UINT16 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load3 Disconnect Enabled N:1-32 | 1 | 0 | 1 | NA | 0x2A35+(N-1)*32 | UINT16 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load4 Disconnect Enabled N:1-32 | 1 | 0 | 1 | NA | 0x2A36+(N-1)*32 | UINT16 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Over Current N:1-32 | 30 | 3 | 40 | A | 0x2A37+(N-1)*32 | UINT16 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load1 Overcurrent Threshold N:1-32 | 30 | 3 | 40 | A | 0x2A38+(N-1)*32 | UINT16 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load2 Overcurrent Threshold N:1-32 | 30 | 3 | 40 | A | 0x2A39+(N-1)*32 | UINT16 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load3 Overcurrent Threshold N:1-32 | 30 | 3 | 40 | A | 0x2A3A+(N-1)*32 | UINT16 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Load4 Overcurrent Threshold N:1-32 | 30 | 3 | 40 | A | 0x2A3B+(N-1)*32 | UINT16 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load Disconnect Voltage N:1-32 | 43.2 | 36 | 56 | V | 0x2A3C+(N-1)*32 | UINT16 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load1 Disconnect Voltage N:1-32 | 43.2 | 36 | 56 | V | 0x2A3D+(N-1)*32 | UINT16 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load2 Disconnect Voltage N:1-32 | 43.2 | 36 | 56 | V | 0x2A3E+(N-1)*32 | UINT16 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load3 Disconnect Voltage N:1-32 | 43.2 | 36 | 56 | V | 0x2A3F+(N-1)*32 | UINT16 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load4 Disconnect Voltage N:1-32 | 43.2 | 36 | 56 | V | 0x2A40+(N-1)*32 | UINT16 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load Reconnect Voltage N:1-32 | 51.5 | 37 | 58 | V | 0x2A41+(N-1)*32 | UINT16 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load1 Reconnect Voltage N:1-32 | 51.5 | 37 | 58 | V | 0x2A42+(N-1)*32 | UINT16 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load2 Reconnect Voltage N:1-32 | 51.5 | 37 | 58 | V | 0x2A43+(N-1)*32 | UINT16 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load3 Reconnect Voltage N:1-32 | 51.5 | 37 | 58 | V | 0x2A44+(N-1)*32 | UINT16 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load4 Reconnect Voltage N:1-32 | 51.5 | 37 | 58 | V | 0x2A45+(N-1)*32 | UINT16 | 1 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load Disconnect Time N:1-32 | 6000 | 0 | 6000 | min | 0x2A46+(N-1)*32 | UINT16 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load1 Disconnect Time N:1-32 | 6000 | 0 | 6000 | min | 0x2A47+(N-1)*32 | UINT16 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load2 Disconnect Time N:1-32 | 6000 | 0 | 6000 | min | 0x2A48+(N-1)*32 | UINT16 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load3 Disconnect Time N:1-32 | 6000 | 0 | 6000 | min | 0x2A49+(N-1)*32 | UINT16 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load4 Disconnect Time N:1-32 | 6000 | 0 | 6000 | min | 0x2A4A+(N-1)*32 | UINT16 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Power Supply Source N:1-32 | 0 | 0 | 10 | NA | 0x2A4B+(N-1)*32 | UINT16 | 0 |  |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
[5 empty] | Register Reserved(0x2A4C~0x2A4F) | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DC Output Distribution Load-iCBD Custom Breaker Capacity N:1-62 | 2000 | 3 | 2000 | A | 0x2A50+(N-1)*16 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DC Output Distribution Load-iCBD Enable Load Disconnect N:1-62 | 0 | 0 | 1 | NA | 0x2A51+(N-1)*16 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DC Output Distribution Load-iCBD Load Disconnect Mode N:1-62 | 0 | 0 | 3 | NA | 0x2A52+(N-1)*16 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DC Output Distribution Load-iCBD Load Disconnect Voltage N:1-62 | 44 | 36 | 56 | V | 0x2A53+(N-1)*16 | UINT16 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DC Output Distribution Load-iCBD Load Reconnect Voltage N:1-62 | 51.5 | 37 | 58 | V | 0x2A54+(N-1)*16 | UINT16 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DC Output Distribution Load-iCBD Load Disconnect Time N:1-62 | 360 | 0 | 6000 | min | 0x2A55+(N-1)*16 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DC Output Distribution Load-iCBD Load Disconnect Capacity N:1-62 | 15 | 0 | 99 | % | 0x2A56+(N-1)*16 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DC Output Distribution Load-iCBD Load Disconnect Energy Consumption N:1-62 | 5 | 0 | 100000 | kWh | 0x2A57~0x2A58+(N-1)*16 | UINT32 | 2 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DC Output Distribution Load-iCBD Heavy Load Alarm Threshold N:1-62 | 80 | 0 | 100 | % | 0x2A59+(N-1)*16 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Register Reserved(0x2A5A~0x2A5F)
Register(0x2E30~0x2FFF) can be used
iDMU M Load-iCBD N Custom Breaker Capacity M:1~4 N:1-34 | 2000 | 3 | 2000 | A | 0x3780+(M-1)*544+(N-1)*16 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDMU M Load-iCBD N Load-iCBD Enable Load Disconnect M:1~4 N:1-34 | 0 | 0 | 1 | NA | 0x3781+(M-1)*544+(N-1)*16 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDMU M Load-iCBD N Load-iCBD Load Disconnect Mode M:1~4 N:1-34 | 0 | 0 | 3 | NA | 0x3782+(M-1)*544+(N-1)*16 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDMU M Load-iCBD N Load-iCBD Load Disconnect Voltage M:1~4 N:1-34 | 44 | 36 | 56 | V | 0x3783+(M-1)*544+(N-1)*16 | UINT16 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDMU M Load-iCBD N Load-iCBD Load Reconnect Voltage M:1~4 N:1-34 | 51.5 | 37 | 58 | V | 0x3784+(M-1)*544+(N-1)*16 | UINT16 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDMU M Load-iCBD N Load-iCBD Load Disconnect Time M:1~4 N:1-34 | 360 | 0 | 6000 | min | 0x3785+(M-1)*544+(N-1)*16 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDMU M Load-iCBD N Load-iCBD Load Disconnect Capacity M:1~4 N:1-34 | 15 | 0 | 99 | % | 0x3786+(M-1)*544+(N-1)*16 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDMU M Load-iCBD N Load-iCBD Load Disconnect Energy Consumption M:1~4 N:1-34 | 5 | 0 | 100000 | kWh | 0x3787~0x3788+(M-1)*544+(N-1)*16 | UINT32 | 2 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDMU M Load-iCBD N Load-iCBD Heavy Load Alarm Threshold M:1~4 N:1-34 | 80 | 0 | 100 | % | 0x3789+(M-1)*544+(N-1)*16 | UINT16 | 0 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Register Reserved(0x378A~0x378F)
Register(0x4000~) Performance Data Used

## Control Parameters
Data | Command Code | Register Address | Data Type | SMU05A V500R001 C30/C50/C60 | SMU02B V300R002 C10/C20 | SMU02B V300R003 C00/C10 | SMU02B V500R001 C00/C10/C20/C30/C50/C60 | SMU02B V500R002 C00 | SMU02B V500R003 C10 | SCC800 V100R001C90 | SMU11D V500R002C50 | SMU V500R003C00(DPS) | SMU11B V500R003C00 | SMU V500R003C10(DPS) | SMU11B V500R003C10 | iSitePower V100R021C10(DPS) | iSitePower V100R021C10(SMU02C/X) | iSitePower V100R021C10(SMU11B) | iSitePower V100R021C10 (Solar cabinet) | iSitePower V100R021C91 (SMU02C/02X) | iSitePower V100R021C91 (PC510-IOT) | iSitePower V100R021C80 (SMU02C/02X) | DP-SP V300R022C00(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C00(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C00(SMU02C/02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C00(SMU11B) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(SMU02C/02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(SMU11B) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(PVPU) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C00(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C00(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C00(SMU02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C10(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C00(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C00(SMU02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C10(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C10(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C10(SMU02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value)
Reset Control | [Yes=1] | 0x3000 | UINT16 | Y | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | N | Y | Y | 0x8001 | 0x2166 | Y | 0x2016 | 0x2166 | Y | 0x2016 | 0x2166 | Y | 0x2016 | 0x2166 | Y | 0x8001 | 0x2166 | Y | 0x2016 | 0x2166 | Y | 0x2016 | 0x2166 | Y | 0x2016 | 0x2166 | Y | 0x8001 | 0x2166 | Y | 0x8001 | 0x2166 | Y | 0x2016 | 0x2166 | Y | 0x2016 | 0x2166 | Y | 0x2016 | 0x2166 | Y | 0x8001 | 0x2166 | Y | 0x2016 | 0x2166 | Y | 0x2016 | 0x2166 | Y | 0x8001 | 0x2166 | Y | 0x2016 | 0x2166
Reset Smoke Sensor | [Yes=1] | 0x3001 | UINT16 | N | Y | Y | Y | Y | Y | N | N | N | Y | N | N | N | Y | N | Y | Y | N | Y | N |  |  | N |  |  | Y | 0x8082 | 0x2149 | N |  |  | N |  |  | N |  |  | Y | 0x8082 | 0x2149 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8082 | 0x2149 | N |  |  | N |  |  | Y | 0x8082 | 0x2149 | N |  |  | N |  |  | Y | 0x8082 | 0x2149
Clear SSU Lost Alarms | [Yes=1] | 0x3002 | UINT16 | N | Y | Y | Y | Y | Y | N | N | N | N | N | N | N | Y | N | Y | Y | N | Y | N |  |  | N |  |  | Y | 0x8011 | 0x2003 | N |  |  | N |  |  | N |  |  | Y | 0x8011 | 0x2003 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8011 | 0x2003 | N |  |  | N |  |  | Y | 0x8011 | 0x2003 | N |  |  | N |  |  | Y | 0x8011 | 0x2003
Battery Charge Control | [float charge=0],[boost charge=1] | 0x3003 | UINT16 | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Battery Standard Test | [Stop test=0],[Test=1] | 0x3004 | UINT16 | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| Registers Reserved | [21 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Battery Cabinet Fan Speed Ratio | [0-100](%) | 0x3010 | UINT16 | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG1 Fault Reset | [Yes=1] | 0x3011 | UINT16 | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG1 Maintenance Confirm | [Yes=1] | 0x3012 | UINT16 | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG1 On/Off Control | [On=0],[Off=1] | 0x3013 | UINT16 | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| Registers Reserved | [21 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG2 On/Off Control | [On=0],[Off=1] | 0x3020 | UINT16 | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG2 Fault Reset | [Yes=1] | 0x3021 | UINT16 | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG2 Maintenance Confirm | [Yes=1] | 0x3022 | UINT16 | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| Registers Reserved | [21 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Air Conditioner 1 Control Mode | [Auto=0],[Manual=1] | 0x3030 | UINT16 | N | Y | Y | Y | Y | Y | N | N | N | Y | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8009 | 0x2017 | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x2017 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x2017 | N |  |  | N |  |  | Y | 0x8009 | 0x2017 | N |  |  | N |  |  | Y | 0x8009 | 0x2017
Air Conditioner 1 Power-on/off | [On=1],[Off=2] | 0x3031 | UINT16 | N | Y | Y | Y | Y | Y | N | N | N | Y | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8009 | 0x2013 | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x2013 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x2013 | N |  |  | N |  |  | Y | 0x8009 | 0x2013 | N |  |  | N |  |  | Y | 0x8009 | 0x2013
Equipment Cabinet Fan Control Mode | [Auto=0],[Manual=1] | 0x3032 | UINT16 | N | Y | Y | Y | Y | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x800C | 0x2005 | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x2005 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x2005 | N |  |  | N |  |  | Y | 0x800C | 0x2005 | N |  |  | N |  |  | Y | 0x800C | 0x2005
Equipment Cabinet Fan Speed Ratio | [0-100](%) | 0x3033 | UINT16 | N | Y | Y | Y | Y | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x800C | 0x2247 | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x2247 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x2247 | N |  |  | N |  |  | Y | 0x800C | 0x2247 | N |  |  | N |  |  | Y | 0x800C | 0x2247
| Registers Reserved | [21 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Air Conditioner 2 Control Mode | [Auto=0],[Manual=1] | 0x3040 | UINT16 | N | Y | Y | Y | Y | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x2004 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2004 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2004 | N |  |  | N |  |  | Y | 0x8022 | 0x2004 | N |  |  | N |  |  | Y | 0x8022 | 0x2004
Air Conditioner 2 Power-on/off | [On=1],[Off=2] | 0x3041 | UINT16 | N | Y | Y | Y | Y | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x2005 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2005 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2005 | N |  |  | N |  |  | Y | 0x8022 | 0x2005 | N |  |  | N |  |  | Y | 0x8022 | 0x2005
Battery Cabinet Fan Control Mode | [Auto=0],[Manual=1] | 0x3042 | UINT16 | N | Y | Y | Y | Y | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x2009 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2009 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2009 | N |  |  | N |  |  | Y | 0x8022 | 0x2009 | N |  |  | N |  |  | Y | 0x8022 | 0x2009
Fan Speed Ratio | [0-100](%) | 0x3043 | UINT16 | N | Y | Y | Y | Y | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x200A | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x200A | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x200A | N |  |  | N |  |  | Y | 0x8022 | 0x200A | N |  |  | N |  |  | Y | 0x8022 | 0x200A
|  | Registers(0x3044~0x304F) Reserved for the TCUX | [20 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Power System Control Mode | [Auto=0],[Manual=1] | 0x3050 | UINT16 | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N | N |  | N | N | N | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | N |  |  | Y |  |  | Y |  |  | Y |  |  | N |  |  | Y |  |  | Y |  |  | N |  |  | Y |  |  | Y |  |  | N
LLVD1 On/Off Control | [On=1],[Off=0] | 0x3051 | UINT16 | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x2159 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2159 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2159 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2159 | N |  |  | N |  |  | Y | 0x8001 | 0x2159 | N
LLVD2 On/Off Control | [On=1],[Off=0] | 0x3052 | UINT16 | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x2160 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2160 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2160 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2160 | N |  |  | N |  |  | Y | 0x8001 | 0x2160 | N
LLVD3 On/Off Control | [On=1],[Off=0] | 0x3053 | UINT16 | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x2165 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2165 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2165 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2165 | N |  |  | N |  |  | Y | 0x8001 | 0x2165 | N
LLVD4 On/Off Control | [On=1],[Off=0] | 0x3054 | UINT16 | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x279D | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x279D | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x279D | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x279D | N |  |  | N |  |  | Y | 0x8001 | 0x279D | N
LLVD5 On/Off Control | [On=1],[Off=0] | 0x3055 | UINT16 | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20D8 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20D8 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20D8 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20D8 | N |  |  | N |  |  | Y | 0x8001 | 0x20D8 | N
LLVD6 On/Off Control | [On=1],[Off=0] | 0x3056 | UINT16 | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20D9 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20D9 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20D9 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20D9 | N |  |  | N |  |  | Y | 0x8001 | 0x20D9 | N
LLVD7 On/Off Control | [On=1],[Off=0] | 0x3057 | UINT16 | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x20DA | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20DA | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20DA | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x20DA | N |  |  | N |  |  | Y | 0x8001 | 0x20DA | N
|  | Registers(0x3058~0x3060) Reserved for LLVD control extends | UINT16 | [19 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers(0x3061~) | UINT16 | [19 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Fan Speed Control N:1-4 |  | 0x3060+(N-1)*4 | UINT16 |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Delete Comm Fail Device N:1-4 | [Yes=1] | 0x3061+(N-1)*4 | UINT16 |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Clear Module Missing Alarm N:1-4 | [Yes=1] | 0x3062+(N-1)*4 | UINT16 |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers(0x3063) Reserved | [20 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Group Clear Module Lost Alarms | [Yes=1] | 0x3070 | UINT16 |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Group Delete Communication Failure Module | [Delete=0] | 0x3071 | UINT16 |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers(0x3072~0x307F) Reserved | UINT16 | [19 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Board All Load Consumption Clear N:1-32 | [Yes=1] | 0x3080+(N-1)*16 | UINT16 |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Board Load1 Consumption Clear N:1-32 | [Yes=1] | 0x3081+(N-1)*16 | UINT16 |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Board Load2 Consumption Clear N:1-32 | [Yes=1] | 0x3082+(N-1)*16 | UINT16 |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Board Load3 Consumption Clear N:1-32 | [Yes=1] | 0x3083+(N-1)*16 | UINT16 |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Board Load4 Consumption Clear N:1-32 | [Yes=1] | 0x3084+(N-1)*16 | UINT16 |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Clear Total Load Overcurrent Alarm N:1-32 | [Yes=0] | 0x3085+(N-1)*16 | UINT16 |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Clear Load1 Overcurrent Protect Alarm N:1-32 | [Yes=0] | 0x3086+(N-1)*16 | UINT16 |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Clear Load2 Overcurrent Protect Alarm N:1-32 | [Yes=0] | 0x3087+(N-1)*16 | UINT16 |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Clear Load3 Overcurrent Protect Alarm N:1-32 | [Yes=0] | 0x3088+(N-1)*16 | UINT16 |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Clear Load4 Overcurrent Protect Alarm N:1-32 | [Yes=0] | 0x3089+(N-1)*16 | UINT16 |  |  |  | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers(0x308A~0x308F) Reserved | [20 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Rectifier N On/Off Control N:1-60 | [On=0],[Off=1] | 0x3280+(N-1) | UINT16 | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers(0x32C0~) | [20 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N

## Performance Data
Data | Unit | Register Address | Data Type | Number of Bytes | Precision | Remarks | SMU05A V500R001 C30/C50/C60 | SMU02B V300R002 C10/C20 | SMU02B V300R003 C00/C10 | SMU02B V500R001 C00/C10/C20/C30/C50/C60 | SMU02B V500R002 C00 | SMU02B V500R003 C10 | SCC800 V100R001C90 | SMU11D V500R002C50 | SMU V500R003C00(DPS) | SMU11B V500R003 C00 | SMU V500R003C10(DPS) | SMU11B V500R003 C10 | iSitePower V100R021C10(DPS) | iSitePower V100R021C10(SMU02C/02X) | iSitePower V100R021C10(SMU11B) | iSitePower V100R021C10 (Solar cabinet) | iSitePower V100R021C91 (SMU02C/02X) | iSitePower V100R021C91 (PC510-IOT) | iSitePower V100R021C80 (SMU02C/02X) | DP-SP V300R022C00(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C00(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C00(SMU02C/02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C00(SMU11B) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(SMU02C/02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(SMU11B) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(PVPU) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C00(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C00(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C00(SMU02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C10(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C00(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C00(SMU02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C10(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C10(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C10(SMU02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value)
Hourly Mains Power Consumption | kWh | 0x4000 | UINT64 | 8 | 2 |  | N | Y | Y | Y | Y | Y | N | Y | Y | N | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x3104 | Y | 0x901C | 0x3001 | Y | 0x901C | 0x3001 | Y | 0x901C | 0x3001 | Y | 0x8001 | 0x3104 | Y | 0x901C | 0x3001 | Y | 0x901C | 0x3001 | Y | 0x901C | 0x3001 | N |  |  | Y | 0x8001 | 0x3104 | Y | 0x901C | 0x3001 | Y | 0x901C | 0x3001 | Y | 0x901C | 0x3001 | Y | 0x8001 | 0x3104 | Y | 0x901C | 0x3001 | Y | 0x901C | 0x3001 | Y | 0x8001 | 0x3104 | Y | 0x901C | 0x3001
Hourly Total DC Load Power Consumption | kWh | 0x4004 | UINT64 | 8 | 2 |  | N | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x3103 | Y | - | - | Y | 0x8232 | 0x31C9 | Y | 0x8226 | 0x3002 | Y | 0x8001 | 0x3103 | Y | - | - | Y | 0x8232 | 0x31C9 | Y | 0x8226 | 0x3002 | Y | 0x8001 | 0x3103 | Y | 0x8001 | 0x3103 | Y | - | - | Y | 0x8232 | 0x31C9 | Y | - | - | Y | 0x8001 | 0x3103 | Y | 0x8232 | 0x31C9 | Y | - | - | Y | 0x8001 | 0x3103 | Y | 0x8232 | 0x31C9
Hourly DG 1 Output Power | kWh | 0x4008 | UINT64 | 8 | 2 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8017 | 0x3001 | N |  |  | N |  |  | N |  |  | Y | 0x8017 | 0x3001 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8017 | 0x3001 | N |  |  | N |  |  | Y | 0x8017 | 0x3001 | N |  |  | N |  |  | Y | 0x8017 | 0x3001
Hourly DG 2 Output Power | kWh | 0x400C | UINT64 | 8 | 2 |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
cumulative Mains Power Consumption | kWh | 0x4010 | UINT64 | 8 | 2 |  | N | Y | Y | Y | Y | Y | N | Y | Y | N | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x3104 | Y | 0x901C | 0x300E | Y | 0x901C | 0x300E | Y | 0x901C | 0x300E | Y | 0x8001 | 0x3104 | Y | 0x901C | 0x300E | Y | 0x901C | 0x300E | Y | 0x901C | 0x300E | N |  |  | Y | 0x8001 | 0x3104 | Y | 0x901C | 0x300E | Y | 0x901C | 0x300E | Y | 0x901C | 0x300E | Y | 0x8001 | 0x3104 | Y | 0x901C | 0x300E | Y | 0x901C | 0x300E | Y | 0x8001 | 0x3104 | Y | 0x901C | 0x300E
cumulative Total DC Load Power Consumption | kWh | 0x4014 | UINT64 | 8 | 2 |  | Y | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x3103 | Y | 0x8001 | 0x1806 | Y | 0x8001 | 0x1806 | Y | 0x8226 | 0x310A | Y | 0x8001 | 0x3103 | Y | 0x8001 | 0x1806 | Y | 0x8001 | 0x1806 | Y | 0x8226 | 0x310A | N |  |  | Y | 0x8001 | 0x3103 | Y | 0x8001 | 0x1806 | Y | 0x8001 | 0x1806 | Y | 0x8001 | 0x1806 | Y | 0x8001 | 0x3103 | Y | 0x8001 | 0x1806 | Y | 0x8001 | 0x1806 | Y | 0x8001 | 0x3103 | Y | 0x8001 | 0x1806
cumulative DG 1 Output Power | kWh | 0x4018 | UINT64 | 8 | 2 |  | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8017 | 0x3001 | N |  |  | N |  |  | N |  |  | Y | 0x8017 | 0x3001 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8017 | 0x3001 | N |  |  | N |  |  | Y | 0x8017 | 0x3001 | N |  |  | N |  |  | Y | 0x8017 | 0x3001
cumulative DG 2 Output Power | kWh | 0x401C | UINT64 | 8 | 2 |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSU Total Output Power | kWh | 0x4020 | UINT64 | 8 | 1 |  | N | N | N | N | N | N | N | N |  | Y |  | Y |  | Y | Y | Y | Y | N | Y | N |  |  | N |  |  | Y | 0x8011 | 0x3002 | Y | 0x8011 | 0x3002 | N |  |  | N |  |  | Y | 0x8011 | 0x3002 | Y | 0x8011 | 0x3002 | Y | 0x8011 | 0x3002 | N |  |  | N |  |  | Y | 0x8011 | 0x3002 | N |  |  | N |  |  | Y | 0x8011 | 0x3002 | N |  |  | N |  |  | Y | 0x8011 | 0x3002
Cumulative Mains Active Power Consumption | kWh | 0x4024 | UINT32 | 4 | 0 | [8 empty] | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x900A | 0x3041 | N |  |  | N |  |  | N |  |  | Y | 0x900A | 0x3041 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x900A | 0x3041 | N |  |  | N |  |  | Y | 0x900A | 0x3041 | N |  |  | N |  |  | Y | 0x900A | 0x3041
Cumulative Mains Active Power Consumption(10Wh) | Wh | 0x4026 | UINT64 | 8 | 0 | [8 empty] | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x900A | 0x3041 | N |  |  | N |  |  | N |  |  | Y | 0x900A | 0x3041 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x900A | 0x3041 | N |  |  | N |  |  | Y | 0x900A | 0x3041 | N |  |  | N |  |  | Y | 0x900A | 0x3041
Cumulative Mains Reactive Power Consumption | kVarh | 0x402A | UINT32 | 4 | 0 | [8 empty] | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x900A | 0x3040 | N |  |  | N |  |  | N |  |  | Y | 0x900A | 0x3040 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x900A | 0x3040 | N |  |  | N |  |  | Y | 0x900A | 0x3040 | N |  |  | N |  |  | Y | 0x900A | 0x3040
Cumulative Mains Reactive Power Consumption(10varh) | Varh | 0x402C | UINT64 | 8 | 0 | [8 empty] | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x900A | 0x3040 | N |  |  | N |  |  | N |  |  | Y | 0x900A | 0x3040 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x900A | 0x3040 | N |  |  | N |  |  | Y | 0x900A | 0x3040 | N |  |  | N |  |  | Y | 0x900A | 0x3040
Cumulative Total Load Power Consumption | kWh | 0x4030 | UINT32 | 4 | 0 | [8 empty] | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8226 | 0x3506 | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3506 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3506 | N |  |  | N |  |  | Y | 0x8226 | 0x3506 | N |  |  | N |  |  | Y | 0x8226 | 0x3506
Cumulative Total Load Power Consumption(10Wh) | Wh | 0x4032 | UINT64 | 8 | 0 | [8 empty] | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8226 | 0x3506 | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3506 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3506 | N |  |  | N |  |  | Y | 0x8226 | 0x3506 | N |  |  | N |  |  | Y | 0x8226 | 0x3506
User1 Cumulative DC Power Consumption | kWh | 0x4036 | UINT32 | 4 | 0 | [8 empty] | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8226 | 0x3500 | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3500 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3500 | N |  |  | N |  |  | Y | 0x8226 | 0x3500 | N |  |  | N |  |  | Y | 0x8226 | 0x3500
User1 Cumulative DC Power Consumption(10Wh) | Wh | 0x4038 | UINT64 | 8 | 0 | [8 empty] | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8226 | 0x3500 | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3500 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3500 | N |  |  | N |  |  | Y | 0x8226 | 0x3500 | N |  |  | N |  |  | Y | 0x8226 | 0x3500
User2 Cumulative DC Power Consumption | kWh | 0x403C | UINT32 | 4 | 0 | [8 empty] | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8226 | 0x3501 | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3501 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3501 | N |  |  | N |  |  | Y | 0x8226 | 0x3501 | N |  |  | N |  |  | Y | 0x8226 | 0x3501
User2 Cumulative DC Power Consumption(10Wh) | Wh | 0x403E | UINT64 | 8 | 0 | [8 empty] | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8226 | 0x3501 | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3501 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3501 | N |  |  | N |  |  | Y | 0x8226 | 0x3501 | N |  |  | N |  |  | Y | 0x8226 | 0x3501
User3 Cumulative DC Power Consumption | kWh | 0x4042 | UINT32 | 4 | 0 | [8 empty] | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8226 | 0x3502 | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3502 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3502 | N |  |  | N |  |  | Y | 0x8226 | 0x3502 | N |  |  | N |  |  | Y | 0x8226 | 0x3502
User3 Cumulative DC Power Consumption(10Wh) | Wh | 0x4044 | UINT64 | 8 | 0 | [8 empty] | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8226 | 0x3502 | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3502 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3502 | N |  |  | N |  |  | Y | 0x8226 | 0x3502 | N |  |  | N |  |  | Y | 0x8226 | 0x3502
User4 Cumulative DC Power Consumption | kWh | 0x4048 | UINT32 | 4 | 0 | [8 empty] | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8226 | 0x3503 | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3503 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3503 | N |  |  | N |  |  | Y | 0x8226 | 0x3503 | N |  |  | N |  |  | Y | 0x8226 | 0x3503
User4 Cumulative DC Power Consumption(10Wh) | Wh | 0x404A | UINT64 | 8 | 0 | [8 empty] | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8226 | 0x3503 | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3503 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3503 | N |  |  | N |  |  | Y | 0x8226 | 0x3503 | N |  |  | N |  |  | Y | 0x8226 | 0x3503
User5 Cumulative DC Power Consumption | kWh | 0x404E | UINT32 | 4 | 0 | [8 empty] | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8226 | 0x3504 | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3504 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3504 | N |  |  | N |  |  | Y | 0x8226 | 0x3504 | N |  |  | N |  |  | Y | 0x8226 | 0x3504
User5 Cumulative DC Power Consumption(10Wh) | Wh | 0x4050 | UINT64 | 8 | 0 | [8 empty] | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8226 | 0x3504 | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3504 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3504 | N |  |  | N |  |  | Y | 0x8226 | 0x3504 | N |  |  | N |  |  | Y | 0x8226 | 0x3504
User6 Cumulative DC Power Consumption | kWh | 0x4054 | UINT32 | 4 | 0 | [8 empty] | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8226 | 0x3505 | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3505 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3505 | N |  |  | N |  |  | Y | 0x8226 | 0x3505 | N |  |  | N |  |  | Y | 0x8226 | 0x3505
User6 Cumulative DC Power Consumption(10Wh) | Wh | 0x4056 | UINT64 | 8 | 0 | [8 empty] | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8226 | 0x3505 | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3505 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3505 | N |  |  | N |  |  | Y | 0x8226 | 0x3505 | N |  |  | N |  |  | Y | 0x8226 | 0x3505
Hourly Mains Power Consumption | kWh | 0x405A | UINT64 | 8 | 2 | AC2 | N | N | N | N | N | Y | N | N | N | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x901C | 0x3001 | N |  |  | N |  |  | N |  |  | Y | 0x901C | 0x3001 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x901C | 0x3001 | N |  |  | N |  |  | Y | 0x901C | 0x3001 | N |  |  | N |  |  | Y | 0x901C | 0x3001
cumulative Mains Power Consumption | kWh | 0x405E | UINT64 | 8 | 2 | AC2 | N | N | N | N | N | Y | N | N | N | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x901C | 0x300E | N |  |  | N |  |  | N |  |  | Y | 0x901C | 0x300E | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x901C | 0x300E | N |  |  | N |  |  | Y | 0x901C | 0x300E | N |  |  | N |  |  | Y | 0x901C | 0x300E
Hourly DC Load1 Power Consumption | kWh | 0x4062 | UINT64 | 8 | 2 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Hourly DC Load2 Power Consumption | kWh | 0x4066 | UINT64 | 8 | 2 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Hourly DC Load3 Power Consumption | kWh | 0x406A | UINT64 | 8 | 2 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Hourly DC Load4 Power Consumption | kWh | 0x406E | UINT64 | 8 | 2 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Hourly DC Load5 Power Consumption | kWh | 0x4072 | UINT64 | 8 | 2 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Hourly DC Load6 Power Consumption | kWh | 0x4076 | UINT64 | 8 | 2 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Hourly DC Load7 Power Consumption | kWh | 0x407A | UINT64 | 8 | 2 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
cumulative DC Load1 Power Consumption | kWh | 0x407E | UINT64 | 8 | 2 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x31F2 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x31F2 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x31F2 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x31F2 | N |  |  | N |  |  | Y | 0x8001 | 0x31F2 | N
cumulative DC Load2 Power Consumption | kWh | 0x4082 | UINT64 | 8 | 2 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x31F3 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x31F3 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x31F3 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x31F3 | N |  |  | N |  |  | Y | 0x8001 | 0x31F3 | N
cumulative DC Load3 Power Consumption | kWh | 0x4086 | UINT64 | 8 | 2 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x31F4 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x31F4 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x31F4 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x31F4 | N |  |  | N |  |  | Y | 0x8001 | 0x31F4 | N
cumulative DC Load4 Power Consumption | kWh | 0x408A | UINT64 | 8 | 2 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x31F5 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x31F5 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x31F5 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x31F5 | N |  |  | N |  |  | Y | 0x8001 | 0x31F5 | N
cumulative DC Load5 Power Consumption | kWh | 0x408E | UINT64 | 8 | 2 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x31F6 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x31F6 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x31F6 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x31F6 | N |  |  | N |  |  | Y | 0x8001 | 0x31F6 | N
cumulative DC Load6 Power Consumption | kWh | 0x4092 | UINT64 | 8 | 2 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x31F7 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x31F7 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x31F7 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x31F7 | N |  |  | N |  |  | Y | 0x8001 | 0x31F7 | N
cumulative DC Load7 Power Consumption | kWh | 0x4096 | UINT64 | 8 | 2 |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x31F8 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x31F8 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x31F8 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x31F8 | N |  |  | N |  |  | Y | 0x8001 | 0x31F8 | N
SSU Total Output Power Consumption per Day | kWh | 0x409A | UINT64 | 8 | 1 |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8011 | 0x3002 | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
|  | Registers Reserved | [11 empty] | N | [11 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
Power consumption of load branch M in combined cabinet N# N: 1–8; M: 1–30 | kWh | 0xB000+(N-1)*60+(M-1)*2 | UINT32 | 4 | 2 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9003 | 0x3031~304E | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x3031~304E | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x3031~304E | N |  |  | N |  |  | Y | 0x9003 | 0x3031~304E | N |  |  | N |  |  | Y | 0x9003 | 0x3031~304E
Power consumption of load branch M for PDU 1 in DC cabinet N# N: 1–14; M: 1–30 | kWh | 0xB1E0+(N-1)*60+(M-1)*2 | UINT32 | 4 | 2 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9002 | 0x1033~0x1050 | N |  |  | N |  |  | N |  |  | Y | 0x9002 | 0x1033~0x1050 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9002 | 0x1033~0x1050 | N |  |  | N |  |  | Y | 0x9002 | 0x1033~0x1050 | N |  |  | N |  |  | Y | 0x9002 | 0x1033~0x1050
Power consumption of load branch M for PDU 2 in DC cabinet N# N: 1–14; M: 1–30 | kWh | 0xB528+(N-1)*60+(M-1)*2 | UINT32 | 4 | 2 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9002 | 0x1051~0x106E | N |  |  | N |  |  | N |  |  | Y | 0x9002 | 0x1051~0x106E | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9002 | 0x1051~0x106E | N |  |  | N |  |  | Y | 0x9002 | 0x1051~0x106E | N |  |  | N |  |  | Y | 0x9002 | 0x1051~0x106E
Power consumption of load branch M for PDU 3 in DC cabinet N# N: 1–14; M: 1–30 | kWh | 0xB870+(N-1)*60+(M-1)*2 | UINT32 | 4 | 2 |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9002 | 0x106F~0x108C | N |  |  | N |  |  | N |  |  | Y | 0x9002 | 0x106F~0x108C | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9002 | 0x106F~0x108C | N |  |  | N |  |  | Y | 0x9002 | 0x106F~0x108C | N |  |  | N |  |  | Y | 0x9002 | 0x106F~0x108C

## Alarm Signals
Data | Register Address | Severity | Parameter Value | Remarks | SMU05A V500R001 C30/C50/C60 | SMU02B V300R002 C10/C20 | SMU02B V300R003 C00/C10 | SMU02B V500R001 C00/C10/C20/C30/C50/C60 | SMU02B V500R002 C00 | SMU02B V500R003 C10 | SCC800 V100R001C90 | SMU11D V500R002C50 | SMU V500R003C00(DPS) | SMU11B V500R003 C00 | SMU V500R003C10(DPS) | SMU11B V500R003 C10 | iSitePower V100R021C10(DPS) | iSitePower V100R021C10 (SMU02C/02X) | iSitePower V100R021C10 (SMU11B) | iSitePower V100R021C10 (Solar cabinet) | iSitePower V100R021C91 (SMU02C/02X) | iSitePower V100R021C91 (PC510-IOT) | iSitePower V100R021C80 (SMU02C/02X) | DP-SP V300R022C00(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C00(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C00(SMU02C/02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C00 (SMU11B) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(SMU02C/02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10 (SMU11B) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R022C10(PVPU) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C00(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C00(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C00(SMU02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | iSitePower V100R023C92(SMU02C/02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R023C10(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C00(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C00(SMU02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C10(DPS A7) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C10(DPS SD5010) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value) | DP-SP V300R024C10(SMU02X) | Mapping Device Type ID | Mapping Signal ID(Partially fixed value)
AC SPD Fault | 0x5000 | MA | 0x00: normal; 0x01: alarm | Summarizes system-level alarms, and reports the alarm when any AC SPD is faulty. | Y | Y | Y | Y | Y | Y | N | Y | N | Y | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x006C | Y | 0x8231 | 0x006C | N |  |  | N |  |  | Y | 0x8231 | 0x006C | Y | 0x8231 | 0x006C | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x006C | Y | 0x8231 | 0x006C | N |  |  | N |  |  | Y | 0x8231 | 0x006C | N |  |  | N |  |  | Y | 0x8231 | 0x006C
DC SPD Fault | 0x5001 | MA | 0x00: normal; 0x01: alarm | Summarizes system-level alarms, and reports the alarm when any DC SPD is faulty. | Y | Y | Y | Y | Y | Y | N | N | N | Y | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8226 | 0x01A4 | Y | 0x8226 | 0x01A4 | N |  |  | N |  |  | Y | 0x8226 | 0x01A4 | Y | 0x8226 | 0x01A4 | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x01A4 | Y | 0x8226 | 0x01A4 | N |  |  | N |  |  | Y | 0x8226 | 0x01A4 | N |  |  | N |  |  | Y | 0x8226 | 0x01A4
AC Failure | 0x5002 | MA | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when the AC power for any cabinet fails. | Y | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x060E | Y | 0x8231 | 0x060E | Y | 0x8231 | 0x060E | Y | 0x8231 | 0x060E | Y | 0x8001 | 0x060E | Y | 0x8231 | 0x060E | Y | 0x8231 | 0x060E | Y | 0x8231 | 0x060E | N |  |  | Y | 0x8001 | 0x060E | Y | 0x8231 | 0x060E | Y | 0x8231 | 0x060E | Y | 0x8231 | 0x060E | Y | 0x8231 | 0x060E | Y | 0x8001 | 0x060E | Y | 0x8231 | 0x060E | Y | 0x8231 | 0x060E | Y | 0x8001 | 0x060E | Y | 0x8231 | 0x060E
AC Phase L1 Overvoltage | 0x5003 | MI | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when the phase L1 AC overvoltage occurs for any cabinet. | Y | Y | Y | Y | Y | Y | N | Y | N | Y | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | Y | 0x8231 | 0x0613 | Y | 0x8231 | 0x0613 | Y | 0x8231 | 0x0613 | N |  |  | Y | 0x8231 | 0x0613 | Y | 0x8231 | 0x0613 | Y | 0x8231 | 0x0613 | N |  |  | N |  |  | Y | 0x8231 | 0x0613 | Y | 0x8231 | 0x0613 | Y | 0x8231 | 0x0613 | Y | 0x8231 | 0x0613 | N |  |  | Y | 0x8231 | 0x0613 | Y | 0x8231 | 0x0613 | N |  |  | Y | 0x8231 | 0x0613
AC Phase L2 Overvoltage | 0x5004 | MI | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when the phase L2 AC overvoltage occurs for any cabinet. | Y | Y | Y | Y | Y | Y | N | Y | N | Y | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | Y | 0x8231 | 0x0614 | Y | 0x8231 | 0x0614 | Y | 0x8231 | 0x0614 | N |  |  | Y | 0x8231 | 0x0614 | Y | 0x8231 | 0x0614 | Y | 0x8231 | 0x0614 | N |  |  | N |  |  | Y | 0x8231 | 0x0614 | Y | 0x8231 | 0x0614 | Y | 0x8231 | 0x0614 | Y | 0x8231 | 0x0614 | N |  |  | Y | 0x8231 | 0x0614 | Y | 0x8231 | 0x0614 | N |  |  | Y | 0x8231 | 0x0614
AC Phase L3 Overvoltage | 0x5005 | MI | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when the phase L3 AC overvoltage occurs for any cabinet. | Y | Y | Y | Y | Y | Y | N | Y | N | Y | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | Y | 0x8231 | 0x0615 | Y | 0x8231 | 0x0615 | Y | 0x8231 | 0x0615 | N |  |  | Y | 0x8231 | 0x0615 | Y | 0x8231 | 0x0615 | Y | 0x8231 | 0x0615 | N |  |  | N |  |  | Y | 0x8231 | 0x0615 | Y | 0x8231 | 0x0615 | Y | 0x8231 | 0x0615 | Y | 0x8231 | 0x0615 | N |  |  | Y | 0x8231 | 0x0615 | Y | 0x8231 | 0x0615 | N |  |  | Y | 0x8231 | 0x0615
AC Phase L1 Undervoltage | 0x5006 | MI | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when the phase L1 AC undervoltage occurs for any cabinet. | Y | Y | Y | Y | Y | Y | N | Y | N | Y | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | Y | 0x8231 | 0x0616 | Y | 0x8231 | 0x0616 | Y | 0x8231 | 0x0616 | N |  |  | Y | 0x8231 | 0x0616 | Y | 0x8231 | 0x0616 | Y | 0x8231 | 0x0616 | N |  |  | N |  |  | Y | 0x8231 | 0x0616 | Y | 0x8231 | 0x0616 | Y | 0x8231 | 0x0616 | Y | 0x8231 | 0x0616 | N |  |  | Y | 0x8231 | 0x0616 | Y | 0x8231 | 0x0616 | N |  |  | Y | 0x8231 | 0x0616
AC Phase L2 Undervoltage | 0x5007 | MI | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when the phase L2 AC undervoltage occurs for any cabinet. | Y | Y | Y | Y | Y | Y | N | Y | N | Y | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | Y | 0x8231 | 0x0617 | Y | 0x8231 | 0x0617 | Y | 0x8231 | 0x0617 | N |  |  | Y | 0x8231 | 0x0617 | Y | 0x8231 | 0x0617 | Y | 0x8231 | 0x0617 | N |  |  | N |  |  | Y | 0x8231 | 0x0617 | Y | 0x8231 | 0x0617 | Y | 0x8231 | 0x0617 | Y | 0x8231 | 0x0617 | N |  |  | Y | 0x8231 | 0x0617 | Y | 0x8231 | 0x0617 | N |  |  | Y | 0x8231 | 0x0617
AC Phase L3 Undervoltage | 0x5008 | MI | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when the phase L3 AC undervoltage occurs for any cabinet. | Y | Y | Y | Y | Y | Y | N | Y | N | Y | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | Y | 0x8231 | 0x0618 | Y | 0x8231 | 0x0618 | Y | 0x8231 | 0x0618 | N |  |  | Y | 0x8231 | 0x0618 | Y | 0x8231 | 0x0618 | Y | 0x8231 | 0x0618 | N |  |  | N |  |  | Y | 0x8231 | 0x0618 | Y | 0x8231 | 0x0618 | Y | 0x8231 | 0x0618 | Y | 0x8231 | 0x0618 | N |  |  | Y | 0x8231 | 0x0618 | Y | 0x8231 | 0x0618 | N |  |  | Y | 0x8231 | 0x0618
AC Phase L1 Failure | 0x5009 | MA | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when the phase L1 open-phase occurs for any cabinet. | Y | Y | Y | Y | Y | Y | N | Y | N | Y | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | Y | 0x8231 | 0x061F | Y | 0x8231 | 0x061F | Y | 0x8231 | 0x061F | N |  |  | Y | 0x8231 | 0x061F | Y | 0x8231 | 0x061F | Y | 0x8231 | 0x061F | N |  |  | N |  |  | Y | 0x8231 | 0x061F | Y | 0x8231 | 0x061F | Y | 0x8231 | 0x061F | Y | 0x8231 | 0x061F | N |  |  | Y | 0x8231 | 0x061F | Y | 0x8231 | 0x061F | N |  |  | Y | 0x8231 | 0x061F
AC Phase L2 Failure | 0x500A | MA | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when the phase L2 open-phase occurs for any cabinet. | Y | Y | Y | Y | Y | Y | N | Y | N | Y | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | Y | 0x8231 | 0x0620 | Y | 0x8231 | 0x0620 | Y | 0x8231 | 0x0620 | N |  |  | Y | 0x8231 | 0x0620 | Y | 0x8231 | 0x0620 | Y | 0x8231 | 0x0620 | N |  |  | N |  |  | Y | 0x8231 | 0x0620 | Y | 0x8231 | 0x0620 | Y | 0x8231 | 0x0620 | Y | 0x8231 | 0x0620 | N |  |  | Y | 0x8231 | 0x0620 | Y | 0x8231 | 0x0620 | N |  |  | Y | 0x8231 | 0x0620
AC Phase L3 Failure | 0x500B | MA | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when the phase L3 open-phase occurs for any cabinet. | Y | Y | Y | Y | Y | Y | N | Y | N | Y | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | Y | 0x8231 | 0x0621 | Y | 0x8231 | 0x0621 | Y | 0x8231 | 0x0621 | N |  |  | Y | 0x8231 | 0x0621 | Y | 0x8231 | 0x0621 | Y | 0x8231 | 0x0621 | N |  |  | N |  |  | Y | 0x8231 | 0x0621 | Y | 0x8231 | 0x0621 | Y | 0x8231 | 0x0621 | Y | 0x8231 | 0x0621 | N |  |  | Y | 0x8231 | 0x0621 | Y | 0x8231 | 0x0621 | N |  |  | Y | 0x8231 | 0x0621
AC Overvoltage | 0x500C | MI | 0x00: normal; 0x01: alarm |  | N | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x0610 | Y | 0x8231 | 0x0610 | Y | 0x8231 | 0x0610 | Y | 0x8231 | 0x0610 | Y | 0x8001 | 0x0610 | Y | 0x8231 | 0x0610 | Y | 0x8231 | 0x0610 | Y | 0x8231 | 0x0610 | N |  |  | Y | 0x8001 | 0x0610 | Y | 0x8231 | 0x0610 | Y | 0x8231 | 0x0610 | Y | 0x8231 | 0x0610 | Y | 0x8231 | 0x0610 | Y | 0x8001 | 0x0610 | Y | 0x8231 | 0x0610 | Y | 0x8231 | 0x0610 | Y | 0x8001 | 0x0610 | Y | 0x8231 | 0x0610
AC Undervoltage | 0x500D | MI | 0x00: normal; 0x01: alarm |  | N | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x0611 | Y | 0x8231 | 0x0611 | Y | 0x8231 | 0x0611 | Y | 0x8231 | 0x0611 | Y | 0x8001 | 0x0611 | Y | 0x8231 | 0x0611 | Y | 0x8231 | 0x0611 | Y | 0x8231 | 0x0611 | N |  |  | Y | 0x8001 | 0x0611 | Y | 0x8231 | 0x0611 | Y | 0x8231 | 0x0611 | Y | 0x8231 | 0x0611 | Y | 0x8231 | 0x0611 | Y | 0x8001 | 0x0611 | Y | 0x8231 | 0x0611 | Y | 0x8231 | 0x0611 | Y | 0x8001 | 0x0611 | Y | 0x8231 | 0x0611
DC Overvoltage | 0x500E | MI | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when DC overvoltage occurs for any cabinet. | Y | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x27A8 | Y | 0x8226 | 0x27A8 | Y | 0x8226 | 0x27A8 | Y | 0x8226 | 0x27A8 | Y | 0x8001 | 0x27A8 | Y | 0x8226 | 0x27A8 | Y | 0x8226 | 0x27A8 | Y | 0x8226 | 0x27A8 | N |  |  | Y | 0x8001 | 0x27A8 | Y | 0x8226 | 0x27A8 | Y | 0x8226 | 0x27A8 | Y | 0x8226 | 0x27A8 | Y | 0x8226 | 0x27A8 | Y | 0x8001 | 0x27A8 | Y | 0x8226 | 0x27A8 | Y | 0x8226 | 0x27A8 | Y | 0x8001 | 0x27A8 | Y | 0x8226 | 0x27A8
DC Undervoltage | 0x500F | MA | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when DC undervoltage occurs for any cabinet. | Y | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0x27A9 | Y | 0x8226 | 0x27A9 | Y | 0x8226 | 0x27A9 | Y | 0x8226 | 0x27A9 | Y | 0x8001 | 0x27A9 | Y | 0x8226 | 0x27A9 | Y | 0x8226 | 0x27A9 | Y | 0x8226 | 0x27A9 | N |  |  | Y | 0x8001 | 0x27A9 | Y | 0x8226 | 0x27A9 | Y | 0x8226 | 0x27A9 | Y | 0x8226 | 0x27A9 | Y | 0x8226 | 0x27A9 | Y | 0x8001 | 0x27A9 | Y | 0x8226 | 0x27A9 | Y | 0x8226 | 0x27A9 | Y | 0x8001 | 0x27A9 | Y | 0x8226 | 0x27A9
Load Fuse Break | 0x5010 | MA | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when any load fuse is blown. | Y | Y | Y | Y | Y | Y | N | Y | N | Y | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | Y | 0x8226 0x830F | 0x27B9 0xF43A | Y | 0x8226 0x830F | 0x27B9 0xF43A | Y | 0x8226 | 0x27B9 | N |  |  | Y | 0x8226 0x830F | 0x27B9 0xF43A | Y | 0x8226 0x830F | 0x27B9 0xF43A | Y | 0x8226 | 0x27B9 | N |  |  | N |  |  | Y | 0x8226 0x830F | 0x27B9 0xF43A | Y | 0x8226 0x830F | 0x27B9 0xF43A | Y | 0x8226 0x830F | 0x27B9 0xF43A | Y | 0x8226 0x830F | 0x27B9 0xF43A | N |  |  | Y | 0x8226 0x830F | 0x27B9 0xF43A | Y | 0x8226 0x830F | 0x27B9 0xF43A | N |  |  | Y | 0x8226 0x830F | 0x27B9 0xF43A
Door Alarm | 0x5011 | MA | 0x00: normal; 0x01: alarm |  | N | Y | Y | Y | Y | Y | N | Y | N | Y | N | Y | N | Y | Y | Y | Y | N | Y | N |  |  | Y | 0x8080 | 0x17CA | Y | 0x8080 | 0x17CA | Y | 0x8080 | 0x17CA | N |  |  | Y | 0x8080 | 0x17CA | Y | 0x8080 | 0x17CA | Y | 0x8080 | 0x17CA | N |  |  | N |  |  | Y | 0x8080 | 0x17CA | Y | 0x8080 | 0x17CA | Y | 0x8080 | 0x17CA | Y | 0x8080 | 0x17CA | N |  |  | Y | 0x8080 | 0x17CA | Y | 0x8080 | 0x17CA | N |  |  | Y | 0x8080 | 0x17CA
Water Alarm | 0x5012 | CA | 0x00: normal; 0x01: alarm |  | N | Y | Y | Y | Y | Y | N | N | N | Y | N | Y | N | Y | Y | Y | Y | N | Y | N |  |  | N |  |  | Y | 0x8081 | 0x17B6 | Y | 0x8081 | 0x17B6 | N |  |  | N |  |  | Y | 0x8081 | 0x17B6 | Y | 0x8081 | 0x17B6 | N |  |  | N |  |  | N |  |  | Y | 0x8081 | 0x17B6 | Y | 0x8081 | 0x17B6 | N |  |  | N |  |  | Y | 0x8081 | 0x17B6 | N |  |  | N |  |  | Y | 0x8081 | 0x17B6
Smoke Alarm | 0x5013 | CA | 0x00: normal; 0x01: alarm |  | N | Y | Y | Y | Y | Y | N | N | N | Y | N | Y | N | Y | Y | Y | Y | N | Y | N |  |  | N |  |  | Y | 0x8082 | 0x17C0 | Y | 0x8082 | 0x17C0 | N |  |  | N |  |  | Y | 0x8082 | 0x17C0 | Y | 0x8082 | 0x17C0 | N |  |  | N |  |  | N |  |  | Y | 0x8082 | 0x17C0 | Y | 0x8082 | 0x17C0 | N |  |  | N |  |  | Y | 0x8082 | 0x17C0 | N |  |  | N |  |  | Y | 0x8082 | 0x17C0
High Equipment Area Temperature | 0x5014 | MI | 0x00: normal; 0x01: alarm | Equipment Cabinet power cabinet-high ambient temperature | N | Y | Y | Y | Y | Y | N | N | N | Y | N | Y | N | Y | Y | Y | Y | N | Y | N |  |  | N |  |  | Y | 0x8083 | 0x01A0 | Y | 0x8083 | 0x01A0 | N |  |  | N |  |  | Y | 0x8083 | 0x01A0 | Y | 0x8083 | 0x01A0 | N |  |  | N |  |  | N |  |  | Y | 0x8083 | 0x01A0 | Y | 0x8083 | 0x01A0 | N |  |  | N |  |  | Y | 0x8083 | 0x01A0 | N |  |  | N |  |  | Y | 0x8083 | 0x01A0
Equipment Area Temperature Sensor Fault | 0x5015 | MA | 0x00: normal; 0x01: alarm | Equipment Cabinet power cabinet-ambient temperature sensor fault | N | Y | Y | Y | Y | Y | N | N | N | Y | N | Y | N | Y | Y | Y | Y | N | Y | N |  |  | N |  |  | Y | 0x8083 | 0x2783 | Y | 0x8083 | 0x2783 | N |  |  | N |  |  | Y | 0x8083 | 0x2783 | Y | 0x8083 | 0x2783 | N |  |  | N |  |  | N |  |  | Y | 0x8083 | 0x2783 | Y | 0x8083 | 0x2783 | N |  |  | N |  |  | Y | 0x8083 | 0x2783 | N |  |  | N |  |  | Y | 0x8083 | 0x2783
Ambient Humidity Sensor Fault | 0x5016 | MI | 0x00: normal; 0x01: alarm | Equipment Cabinet ambient humidity sensor fault | N | Y | Y | Y | Y | Y | N | N | N | Y | N | Y | N | Y | Y | Y | Y | N | Y | N |  |  | N |  |  | Y | 0x8083 | 0x277F | Y | 0x8083 | 0x277F | N |  |  | N |  |  | Y | 0x8083 | 0x277F | Y | 0x8083 | 0x277F | N |  |  | N |  |  | N |  |  | Y | 0x8083 | 0x277F | Y | 0x8083 | 0x277F | N |  |  | N |  |  | Y | 0x8083 | 0x277F | N |  |  | N |  |  | Y | 0x8083 | 0x277F
LLVD1 Warning | 0x5017 | MA | 0x00: normal; 0x01: alarm |  | Y | Y | Y | Y | Y | Y | N | N | N | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0xF291 | N |  |  | Y | 0x8226 0x830F | 0x2774 0xF452 | Y | 0x8226 | 0x2774 | Y | 0x8001 | 0xF291 | N |  |  | Y | 0x8226 0x830F | 0x2774 0xF452 | Y | 0x8226 | 0x2774 | N |  |  | Y | 0x8001 | 0xF291 | N |  |  | Y | 0x8226 0x830F | 0x2774 0xF452 | Y | 0x8226 0x830F | 0x2774 0xF452 | N |  |  | Y | 0x8001 | 0xF291 | Y | 0x8226 0x830F | 0x2774 0xF452 | N |  |  | Y | 0x8001 | 0xF291 | Y | 0x8226 0x830F | 0x2774 0xF452
LLVD1 Disconnected | 0x5018 | MA | 0x00: normal; 0x01: alarm |  | Y | Y | Y | Y | Y | Y | N | N | N | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0xF298 | N |  |  | Y | 0x8226 0x830F | 0xF014 0xF43E | Y | 0x8226 | 0x2276/0x5133~0x5136/0xF014 | Y | 0x8001 | 0xF298 | N |  |  | Y | 0x8226 0x830F | 0xF014 0xF43E | Y | 0x8226 | 0x2276/0x5133~0x5136/0xF014 | N |  |  | Y | 0x8001 | 0xF298 | N |  |  | Y | 0x8226 0x830F | 0xF014 0xF43E | Y | 0x8226 0x830F | 0xF014 0xF43E | N |  |  | Y | 0x8001 | 0xF298 | Y | 0x8226 0x830F | 0xF014 0xF43E | N |  |  | Y | 0x8001 | 0xF298 | Y | 0x8226 0x830F | 0xF014 0xF43E
LLVD2 Warning | 0x5019 | MA | 0x00: normal; 0x01: alarm |  | N | Y | Y | Y | Y | Y | N | N | N | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0xF292 | N |  |  | Y | 0x8226 | 0x2778 | Y | 0x8226 | 0x2778 | Y | 0x8001 | 0xF292 | N |  |  | Y | 0x8226 | 0x2778 | Y | 0x8226 | 0x2778 | N |  |  | Y | 0x8001 | 0xF292 | N |  |  | Y | 0x8226 | 0x2778 | Y | 0x8226 | 0x2778 | N |  |  | Y | 0x8001 | 0xF292 | Y | 0x8226 | 0x2778 | N |  |  | Y | 0x8001 | 0xF292 | Y | 0x8226 | 0x2778
LLVD2 Disconnected | 0x501A | MA | 0x00: normal; 0x01: alarm |  | N | Y | Y | Y | Y | Y | N | N | N | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8001 | 0xF299 | N |  |  | Y | 0x8226 | 0xF015 | Y | 0x8226 | 0x2279/0x5139~0x513C/0xF015 | Y | 0x8001 | 0xF299 | N |  |  | Y | 0x8226 | 0xF015 | Y | 0x8226 | 0x2279/0x5139~0x513C/0xF015 | N |  |  | Y | 0x8001 | 0xF299 | N |  |  | Y | 0x8226 | 0xF015 | Y | 0x8226 | 0xF015 | N |  |  | Y | 0x8001 | 0xF299 | Y | 0x8226 | 0xF015 | N |  |  | Y | 0x8001 | 0xF299 | Y | 0x8226 | 0xF015
DC Ultra High Voltage | 0x501B | MA | 0x00: normal; 0x01: alarm | [8 empty] | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8226 | 0x27AA | Y | 0x8226 | 0x27AA | N |  |  | N |  |  | Y | 0x8226 | 0x27AA | Y | 0x8226 | 0x27AA | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x27AA | Y | 0x8226 | 0x27AA | Y | 0x8226 | 0x27AA | Y | 0x8226 | 0x27AA | N |  |  | Y | 0x8226 | 0x27AA | Y | 0x8226 | 0x27AA | N |  |  | Y | 0x8226 | 0x27AA
DC Ultra Low Voltage | 0x501C | MA | 0x00: normal; 0x01: alarm | [8 empty] | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8226 | 0x27AB | Y | 0x8226 | 0x27AB | N |  |  | N |  |  | Y | 0x8226 | 0x27AB | Y | 0x8226 | 0x27AB | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x27AB | Y | 0x8226 | 0x27AB | Y | 0x8226 | 0x27AB | Y | 0x8226 | 0x27AB | N |  |  | Y | 0x8226 | 0x27AB | Y | 0x8226 | 0x27AB | N |  |  | Y | 0x8226 | 0x27AB
Controller Hardware Fault | 0x501D | MA | 0x00: normal; 0x01: alarm | [8 empty] | N | Y | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8001 | 0xF000 | Y | 0x2016 | 0xF000 | Y | 0x2016 | 0xF000 | N |  |  | Y | 0x8001 | 0xF000 | Y | 0x2016 | 0xF000 | Y | 0x2016 | 0xF000 | N |  |  | Y | 0x8001 | 0xF000 | Y | 0x8001 | 0xF000 | Y | 0x2016 | 0xF000 | Y | 0x2016 | 0xF000 | Y | 0x2016 | 0xF000 | Y | 0x2016 | 0xF000 | Y | 0x8001 | 0xF000 | Y | 0x2016 | 0xF000 | Y | 0x2016 | 0xF000 | Y | 0x8001 | 0xF000 | Y | 0x2016 | 0xF000
Battery Test Failure | 0x501E | MA | 0x00: normal; 0x01: alarm | [8 empty] | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x29EC | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x29EC | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x29EC | Y | 0x8004 | 0x29EC | N |  |  | N |  |  | Y | 0x8004 | 0x29EC | N |  |  | N |  |  | Y | 0x8004 | 0x29EC
LVD Disabled | 0x501F | MA | 0x00: normal; 0x01: alarm | [14 empty] | Y |  |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8226 | 0x3BE3 | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3BE3 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8226 | 0x3BE3 | Y | 0x8226 | 0x3BE3 | N |  |  | N |  |  | Y | 0x8226 | 0x3BE3 | N |  |  | N |  |  | Y | 0x8226 | 0x3BE3
Low Rectifier Remaining Capacity | 0x5020 | MA | 0x00: normal; 0x01: alarm | [8 empty] | N | Y | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8003 | 0x226A | Y | 0x8003 | 0x226A | Y | 0x8003 | 0x226A | N |  |  | Y | 0x8003 | 0x226A | Y | 0x8003 | 0x226A | Y | 0x8003 | 0x226A | N |  |  | N |  |  | Y | 0x8003 | 0x226A | Y | 0x8003 | 0x226A | Y | 0x8003 | 0x226A | Y | 0x8003 | 0x226A | Y | 0x8003 | 0x226A | Y | 0x8003 | 0x226A | Y | 0x8003 | 0x226A | Y | 0x8003 | 0x226A | Y | 0x8003 | 0x226A | Y | 0x8003 | 0x226A
Battery Discharge | 0x5021 | MA | 0x00: normal; 0x01: alarm | [8 empty] | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x02E0 | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x02E0 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x02E0 | Y | 0x8004 | 0x02E0 | N |  |  | N |  |  | Y | 0x8004 | 0x02E0 | N |  |  | N |  |  | Y | 0x8004 | 0x02E0
Battery Missing | 0x5022 | MA | 0x00: normal; 0x01: alarm | [8 empty] | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8018 | 0x35FD | N |  |  | N |  |  | N |  |  | Y | 0x8018 | 0x35FD | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8018 | 0x35FD | Y | 0x8018 | 0x35FD | N |  |  | N |  |  | Y | 0x8018 | 0x35FD | N |  |  | N |  |  | Y | 0x8018 | 0x35FD
DI1~DI12 | 0x5023~0x502E | MI | 0x00: normal; 0x01: alarm | Digital input alarm | [7 empty] | N | Y | N | Y | N | Y |  | N |  |  | N |  | Y | 0x8001 | 0x283D~0x283E | Y | 0x9032 | 0x283D~0x2842 | N |  |  | N |  |  | Y | 0x8001 | 0x283D~0x283E | Y | 0x9032 | 0x283D~0x2842 | N |  |  | N |  |  | Y | 0x8001 | 0x283D | Y | 0x8001 | 0x283D~0x283E | Y | 0x9032 | 0x283D~0x2842 | N |  |  | N |  |  | Y | 0x9032 | 0x283D~0x2842 | Y | 0x8001 | 0x283D~0x283E | N |  |  | Y | 0x9032 | 0x283D~0x2842 | Y | 0x8001 | 0x283D~0x283E | N
Urgent Alarm (not standard, for special customer CELLNEX) | 0x502F | MA | 0x00: normal; 0x01: alarm | user defined | [7 empty] | N | N | N | N | N | N |  | N |  |  | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Non-urgent Alarm (not standard, for special customer CELLNEX) | 0x5030 | MI | 0x00: normal; 0x01: alarm | user defined | [7 empty] | N | N | N | N | N | N |  | N |  |  | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Fuse Broken Alarm (not standard, for special customer CELLNEX) | 0x5031 | MA | 0x00: normal; 0x01: alarm | user defined: load fuse broken and battery fuse broken | [7 empty] | N | N | N | N | N | N |  | N |  |  | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
LLVD3 Warning | 0x5032 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0xF293 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF293 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF293 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF293 | N |  |  | N |  |  | Y | 0x8001 | 0xF293 | N
LLVD3 Disconnected | 0x5033 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0xF29A | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF29A | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF29A | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF29A | N |  |  | N |  |  | Y | 0x8001 | 0xF29A | N
LLVD4 Warning | 0x5034 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0xF294 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF294 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF294 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF294 | N |  |  | N |  |  | Y | 0x8001 | 0xF294 | N
LLVD4 Disconnected | 0x5035 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0xF29B | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF29B | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF29B | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF29B | N |  |  | N |  |  | Y | 0x8001 | 0xF29B | N
Lithium Battery N Abnormal (N: 1–32) | 0x5036+ (N-1)*1 | MA | 0x00: normal 0x01: Fault 0x02: Protection 0x03: Communication Fail |  | N | N | N | N | N | Y | N | Y | Y | N | Y | N | Y | Y | N |  | Y | N | Y | Y | 0x8018 0x8019 0x8019 0x8019 | 0x35E8 0x35B6 0x35B7~0x35B8/0x35C8~0x35D7/0x5867 0x35BB/0x35C1/0x35C3/0x35C5/0x35C7/0xF0C4 | Y | 0x8018 0x8019 | 0x35E8 0x35B6/0x5867/0x35E1/0x35E2/0xF020/0xF021/0xF022/0xF0C4 | Y | 0x8018 | 0x1113~0x1132 | N |  |  | Y | 0x8018 0x8019 0x8019 0x8019 | 0x35E8 0x35B6 0x35B7~0x35B8/0x35C8~0x35D7/0x5867 0x35BB/0x35C1/0x35C3/0x35C5/0x35C7/0xF0C4 | Y | 0x8018 0x8019 | 0x35E8 0x35B6/0x5867/0x35E1/0x35E2/0xF020/0xF021/0xF022/0xF0C4 | Y | 0x8018 | 0x1113~0x1132 | N |  |  | Y | 0x8018 0x8019 | 0x35E8 0x35B6/0x5867/0x35E1/0x35E2/0xF0C4 | Y | 0x8018 0x8019 0x8019 0x8019 | 0x35E8 0x35B6 0x35B7~0x35B8/0x35C8~0x35D7/0x5867 0x35BB/0x35C1/0x35C3/0x35C5/0x35C7/0xF0C4 | Y | 0x8018 0x8019 | 0x35E8 0x35B6/0x5867/0x35E1/0x35E2/0xF020/0xF021/0xF022/0xF0C4 | Y | 0x8018 | 0x1113~0x1132 | Y | 0x8018 | 0x1113~0x1132 | Y | 0x8018 0x8019 | 0x35E8 0x35B6/0x5867/0x35E1/0x35E2/0xF020/0xF021/0xF022/0xF0C4 | Y | 0x8018 0x8019 0x8019 0x8019 | 0x35E8 0x35B6 0x35B7~0x35B8/0x35C8~0x35D7/0x5867 0x35BB/0x35C1/0x35C3/0x35C5/0x35C7/0xF0C4 | Y | 0x8018 | 0x1113~0x1132 | Y | 0x8018 0x8019 | 0x35E8 0x35B6/0x5867/0x35E1/0x35E2/0xF020/0xF021/0xF022/0xF0C4 | Y | 0x8018 0x8019 0x8019 0x8019 | 0x35E8 0x35B6 0x35B7~0x35B8/0x35C8~0x35D7/0x5867 0x35BB/0x35C1/0x35C3/0x35C5/0x35C7/0xF0C4 | Y | 0x8018 | 0x1113~0x1132
LLVD5 Warning | 0x5056 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0xF295 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF295 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF295 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF295 | N |  |  | N |  |  | Y | 0x8001 | 0xF295 | N
LLVD5 Disconnected | 0x5057 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0xF29C | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF29C | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF29C | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF29C | N |  |  | N |  |  | Y | 0x8001 | 0xF29C | N
LLVD6 Warning | 0x5058 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0xF296 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF296 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF296 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF296 | N |  |  | N |  |  | Y | 0x8001 | 0xF296 | N
LLVD6 Disconnected | 0x5059 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0xF29D | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF29D | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF29D | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF29D | N |  |  | N |  |  | Y | 0x8001 | 0xF29D | N
LLVD7 Warning | 0x505A | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0xF297 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF297 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF297 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF297 | N |  |  | N |  |  | Y | 0x8001 | 0xF297 | N
LLVD7 Disconnected | 0x505B | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | Y | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0xF29E | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF29E | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF29E | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0xF29E | N |  |  | N |  |  | Y | 0x8001 | 0xF29E | N
AC Line L1L2 Overvoltage | 0x505C | MI | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when the line L1L2 AC overvoltage occurs for any cabinet. | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x281E | Y | 0x8231 | 0x281E | N |  |  | N |  |  | Y | 0x8001 | 0x281E | Y | 0x8231 | 0x281E | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x281E | Y | 0x8231 | 0x281E | N |  |  | N |  |  | Y | 0x8231 | 0x281E | Y | 0x8001 | 0x281E | N |  |  | Y | 0x8231 | 0x281E | Y | 0x8001 | 0x281E | N
AC Line L2L3 Overvoltage | 0x505D | MI | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when the line L2L3 AC overvoltage occurs for any cabinet. | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x281F | Y | 0x8231 | 0x281F | N |  |  | N |  |  | Y | 0x8001 | 0x281F | Y | 0x8231 | 0x281F | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x281F | Y | 0x8231 | 0x281F | N |  |  | N |  |  | Y | 0x8231 | 0x281F | Y | 0x8001 | 0x281F | N |  |  | Y | 0x8231 | 0x281F | Y | 0x8001 | 0x281F | N
AC Line L3L1 Overvoltage | 0x505E | MI | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when the line L3L1 AC overvoltage occurs for any cabinet. | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x2820 | Y | 0x8231 | 0x2820 | N |  |  | N |  |  | Y | 0x8001 | 0x2820 | Y | 0x8231 | 0x2820 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2820 | Y | 0x8231 | 0x2820 | N |  |  | N |  |  | Y | 0x8231 | 0x2820 | Y | 0x8001 | 0x2820 | N |  |  | Y | 0x8231 | 0x2820 | Y | 0x8001 | 0x2820 | N
AC Line L1L2 Undervoltage | 0x505F | MI | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when the line L1L2 AC undervoltage occurs for any cabinet. | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x2821 | Y | 0x8231 | 0x2821 | N |  |  | N |  |  | Y | 0x8001 | 0x2821 | Y | 0x8231 | 0x2821 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2821 | Y | 0x8231 | 0x2821 | N |  |  | N |  |  | Y | 0x8231 | 0x2821 | Y | 0x8001 | 0x2821 | N |  |  | Y | 0x8231 | 0x2821 | Y | 0x8001 | 0x2821 | N
AC Line L2L3 Undervoltage | 0x5060 | MI | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when the line L2L3 AC undervoltage occurs for any cabinet. | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x2822 | Y | 0x8231 | 0x2822 | N |  |  | N |  |  | Y | 0x8001 | 0x2822 | Y | 0x8231 | 0x2822 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2822 | Y | 0x8231 | 0x2822 | N |  |  | N |  |  | Y | 0x8231 | 0x2822 | Y | 0x8001 | 0x2822 | N |  |  | Y | 0x8231 | 0x2822 | Y | 0x8001 | 0x2822 | N
AC Line L3L1 Undervoltage | 0x5061 | MI | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when the line L3L1 AC undervoltage occurs for any cabinet. | N | N | N | N | N | N | N | N | N | N | N | N | Y | N | N |  | N | N | N | Y | 0x8001 | 0x2823 | Y | 0x8231 | 0x2823 | N |  |  | N |  |  | Y | 0x8001 | 0x2823 | Y | 0x8231 | 0x2823 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x2823 | Y | 0x8231 | 0x2823 | N |  |  | N |  |  | Y | 0x8231 | 0x2823 | Y | 0x8001 | 0x2823 | N |  |  | Y | 0x8231 | 0x2823 | Y | 0x8001 | 0x2823 | N
Main AC Breaker Trip | 0x5062 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SMU Fault | 0x5063 | MA | 0x00: normal; 0x01: alarm | When detecting a fault in itself, the SMU generates an SMU Fault alarm. | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
UIM Temp1 High Temperature | 0x5064 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
UIM Temp1 Low Temperature | 0x5065 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
UIM Temp2 High Temperature | 0x5066 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
UIM Temp2 Low Temperature | 0x5067 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AC SPD2 Fault | 0x5068 | MA | 0x00: normal; 0x01: alarm | Summarizes system-level alarms, and reports the alarm when any AC SPD2 is faulty. | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| Registers(0x5068~0x506F) Reserved | [10 empty] | N | [11 empty] | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N | [5 empty] | N |  |  | N
DC Failure | 0x5070 | MA | 0x00: normal; 0x01: alarm | [9 empty] | Y | N | Y | N | Y |  | N |  |  | N |  | Y | 0x8001 | 0x3BA6 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x3BA6 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x3BA6 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x3BA6 | N |  |  | N |  |  | Y | 0x8001 | 0x3BA6 | N
DC Input Overvoltage | 0x5071 | MI | 0x00: normal; 0x01: alarm | [9 empty] | Y | N | Y | N | Y |  | N |  |  | N |  | Y | 0x8001 | 0x3BA1 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x3BA1 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x3BA1 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x3BA1 | N |  |  | N |  |  | Y | 0x8001 | 0x3BA1 | N
DC Input Undervoltage | 0x5072 | MI | 0x00: normal; 0x01: alarm | [9 empty] | Y | N | Y | N | Y |  | N |  |  | N |  | Y | 0x8001 | 0x3BA2 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x3BA2 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x3BA2 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x3BA2 | N |  |  | N |  |  | Y | 0x8001 | 0x3BA2 | N
Parallel Fail | 0x5073 | MA | 0x00: normal; 0x01: alarm | [9 empty] | Y | N | Y | N | Y |  | N |  |  | N |  | Y | 0x8001 | 0x3BA3 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x3BA3 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x3BA3 | Y | 0x8001 | 0x3BA3 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x3BA3 | N |  |  | N |  |  | Y | 0x8001 | 0x3BA3 | N
Parallel Address Conflict | 0x5074 | MA | 0x00: normal; 0x01: alarm | [9 empty] | Y | N | Y | N | Y |  | N |  |  | N |  | Y | 0x8001 | 0x3BA4 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x3BA4 | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x3BA4 | Y | 0x8001 | 0x3BA4 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8001 | 0x3BA4 | N |  |  | N |  |  | Y | 0x8001 | 0x3BA4 | N
Rectifier Upgrade Fault | 0x5075 | MA | 0x00: normal; 0x01: alarm | [9 empty] | Y | N | Y | N | Y |  | N |  |  | N |  | Y | 0x8003 | 0x2267 | N |  |  | N |  |  | N |  |  | Y | 0x8003 | 0x2267 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8003 | 0x2267 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8003 | 0x2267 | N |  |  | N |  |  | Y | 0x8003 | 0x2267 | N
AC SPD Fault | 0x5076 | MA | 0x00: normal; 0x01: alarm | AC2 Summarizes system-level alarms, and reports the alarm when any AC SPD is faulty. | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x006C | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x006C | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x006C | Y | 0x8231 | 0x006C | N |  |  | N |  |  | Y | 0x8231 | 0x006C | N |  |  | N |  |  | Y | 0x8231 | 0x006C
AC Failure | 0x5077 | MA | 0x00: normal; 0x01: alarm | AC2 Summarizes system-level alarms and reports the alarm when the AC power for any cabinet fails. | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x060E | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x060E | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x060E | Y | 0x8231 | 0x060E | N |  |  | N |  |  | Y | 0x8231 | 0x060E | N |  |  | N |  |  | Y | 0x8231 | 0x060E
AC Phase L1 Overvoltage | 0x5078 | MI | 0x00: normal; 0x01: alarm | AC2 Summarizes system-level alarms and reports the alarm when the phase L1 AC overvoltage occurs for any cabinet. | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x0613 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x0613 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x0613 | Y | 0x8231 | 0x0613 | N |  |  | N |  |  | Y | 0x8231 | 0x0613 | N |  |  | N |  |  | Y | 0x8231 | 0x0613
AC Phase L2 Overvoltage | 0x5079 | MI | 0x00: normal; 0x01: alarm | AC2 Summarizes system-level alarms and reports the alarm when the phase L2 AC overvoltage occurs for any cabinet. | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x0614 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x0614 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x0614 | Y | 0x8231 | 0x0614 | N |  |  | N |  |  | Y | 0x8231 | 0x0614 | N |  |  | N |  |  | Y | 0x8231 | 0x0614
AC Phase L3 Overvoltage | 0x507A | MI | 0x00: normal; 0x01: alarm | AC2 Summarizes system-level alarms and reports the alarm when the phase L3 AC overvoltage occurs for any cabinet. | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x0615 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x0615 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x0615 | Y | 0x8231 | 0x0615 | N |  |  | N |  |  | Y | 0x8231 | 0x0615 | N |  |  | N |  |  | Y | 0x8231 | 0x0615
AC Phase L1 Undervoltage | 0x507B | MI | 0x00: normal; 0x01: alarm | AC2 Summarizes system-level alarms and reports the alarm when the phase L1 AC undervoltage occurs for any cabinet. | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x0616 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x0616 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x0616 | Y | 0x8231 | 0x0616 | N |  |  | N |  |  | Y | 0x8231 | 0x0616 | N |  |  | N |  |  | Y | 0x8231 | 0x0616
AC Phase L2 Undervoltage | 0x507C | MI | 0x00: normal; 0x01: alarm | AC2 Summarizes system-level alarms and reports the alarm when the phase L2 AC undervoltage occurs for any cabinet. | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x0617 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x0617 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x0617 | Y | 0x8231 | 0x0617 | N |  |  | N |  |  | Y | 0x8231 | 0x0617 | N |  |  | N |  |  | Y | 0x8231 | 0x0617
AC Phase L3 Undervoltage | 0x507D | MI | 0x00: normal; 0x01: alarm | AC2 Summarizes system-level alarms and reports the alarm when the phase L3 AC undervoltage occurs for any cabinet. | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x0618 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x0618 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x0618 | Y | 0x8231 | 0x0618 | N |  |  | N |  |  | Y | 0x8231 | 0x0618 | N |  |  | N |  |  | Y | 0x8231 | 0x0618
AC Phase L1 Failure | 0x507E | MA | 0x00: normal; 0x01: alarm | AC2 Summarizes system-level alarms and reports the alarm when the phase L1 open-phase occurs for any cabinet. | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x061F | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x061F | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x061F | Y | 0x8231 | 0x061F | N |  |  | N |  |  | Y | 0x8231 | 0x061F | N |  |  | N |  |  | Y | 0x8231 | 0x061F
AC Phase L2 Failure | 0x507F | MA | 0x00: normal; 0x01: alarm | AC2 Summarizes system-level alarms and reports the alarm when the phase L2 open-phase occurs for any cabinet. | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x0620 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x0620 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x0620 | Y | 0x8231 | 0x0620 | N |  |  | N |  |  | Y | 0x8231 | 0x0620 | N |  |  | N |  |  | Y | 0x8231 | 0x0620
AC Phase L3 Failure | 0x5080 | MA | 0x00: normal; 0x01: alarm | AC2 Summarizes system-level alarms and reports the alarm when the phase L3 open-phase occurs for any cabinet. | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x0621 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x0621 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x0621 | Y | 0x8231 | 0x0621 | N |  |  | N |  |  | Y | 0x8231 | 0x0621 | N |  |  | N |  |  | Y | 0x8231 | 0x0621
AC Overvoltage | 0x5081 | MI | 0x00: normal; 0x01: alarm | AC2 | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x0610 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x0610 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x0610 | Y | 0x8231 | 0x0610 | N |  |  | N |  |  | Y | 0x8231 | 0x0610 | N |  |  | N |  |  | Y | 0x8231 | 0x0610
AC Undervoltage | 0x5082 | MI | 0x00: normal; 0x01: alarm | AC2 | N | N | N | N | N | Y | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x0611 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x0611 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x0611 | Y | 0x8231 | 0x0611 | N |  |  | N |  |  | Y | 0x8231 | 0x0611 | N |  |  | N |  |  | Y | 0x8231 | 0x0611
Main AC Breaker Trip | 0x5083 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| Registers Reserved | [20 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Rectifier Missing | 0x5100 | MA | 0x00: normal; 0x01: alarm | Rectifier missing, systematic level, summarization SD5010 DPS no support | Y | Y | Y | Y | Y | Y | N | N | N | Y | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | Y | 0x8003 | 0x2262 | Y | 0x8003 | 0x2262 | Y | 0x8003 | 0x2262 | N |  |  | Y | 0x8003 | 0x2262 | Y | 0x8003 | 0x2262 | Y | 0x8003 | 0x2262 | N |  |  | N |  |  | Y | 0x8003 | 0x2262 | Y | 0x8003 | 0x2262 | Y | 0x8003 | 0x2262 | Y | 0x8003 | 0x2262 | N |  |  | Y | 0x8003 | 0x2262 | Y | 0x8003 | 0x2262 | N |  |  | Y | 0x8003 | 0x2262
Rectifier Abnormal | 0x5101 | MA | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when any rectifier generates these alarms(Communication Failure, Rectifier Power Failure, Rectifier Fault, Rectifier Protection, Rectifier Over Voltage). | Y | N | N | N | N | Y | N | N | N | N | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | Y | 0x8003 | 0x107A | Y | 0x8003 | 0x107A | Y | 0x8003 | 0x107A | N |  |  | Y | 0x8003 | 0x107A | Y | 0x8003 | 0x107A | Y | 0x8003 | 0x107A | N |  |  | N |  |  | Y | 0x8003 | 0x107A | Y | 0x8003 | 0x107A | Y | 0x8003 | 0x107A | Y | 0x8003 | 0x107A | N |  |  | Y | 0x8003 | 0x107A | Y | 0x8003 | 0x107A | N |  |  | Y | 0x8003 | 0x107A
All Rectifiers Communication Failure | 0x5102 | MA | 0x00: normal; 0x01: alarm | All Rectifiers Communication Failure | [7 empty] | N | N | N | N |  | N | Y |  |  | Y | N | Y | N |  |  | Y | 0x8003 | 0x2260 | Y | 0x8003 | 0x2260 | N |  |  | N |  |  | Y | 0x8003 | 0x2260 | Y | 0x8003 | 0x2260 | N |  |  | N |  |  | N |  |  | Y | 0x8003 | 0x2260 | Y | 0x8003 | 0x2260 | Y | 0x8003 | 0x2260 | Y | 0x8003 | 0x2260 | N |  |  | Y | 0x8003 | 0x2260 | Y | 0x8003 | 0x2260 | N |  |  | Y | 0x8003 | 0x2260
Multi-Rectifier Fault | 0x5103 |  | 0x00: normal; 0x01: alarm | [14 empty] | Y |  |  | Y | N | Y | N |  |  | Y | 0x8003 | 0x2266 | Y | 0x8003 | 0x2266 | N |  |  | N |  |  | Y | 0x8003 | 0x2266 | Y | 0x8003 | 0x2266 | N |  |  | N |  |  | N |  |  | Y | 0x8003 | 0x2266 | Y | 0x8003 | 0x2266 | Y | 0x8003 | 0x2266 | Y | 0x8003 | 0x2266 | N |  |  | Y | 0x8003 | 0x2266 | Y | 0x8003 | 0x2266 | N |  |  | Y | 0x8003 | 0x2266
| Registers Reserved | [20 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Rectifier N Fault (N: 1–60) | 0x5120 + (N-1) *16 | MA | 0x00: normal; 0x01: alarm | /Rectifier N fault | N | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8002 | 0x0644 | Y | 0x8002 | 0x0644 | Y | 0x8002 | 0x0644 | Y | 0x8002 | 0x0644 | Y | 0x8002 | 0x0644 | Y | 0x8002 | 0x0644 | Y | 0x8002 | 0x0644 | Y | 0x8002 | 0x0644 | N |  |  | Y | 0x8002 | 0x0644 | Y | 0x8002 | 0x0644 | Y | 0x8002 | 0x0644 | Y | 0x8002 | 0x0644 | Y | 0x8002 | 0x0644 | Y | 0x8002 | 0x0644 | Y | 0x8002 | 0x0644 | Y | 0x8002 | 0x0644 | Y | 0x8002 | 0x0644 | Y | 0x8002 | 0x0644
Rectifier N Protection (N: 1–60) | 0x5121 + (N-1) *16 | MI | 0x00: normal; 0x01: alarm | /Rectifier N protection | N | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8002 | 0x0643 | Y | 0x8002 | 0x0643 | Y | 0x8002 | 0x0643 | Y | 0x8002 | 0x0643 | Y | 0x8002 | 0x0643 | Y | 0x8002 | 0x0643 | Y | 0x8002 | 0x0643 | Y | 0x8002 | 0x0643 | N |  |  | Y | 0x8002 | 0x0643 | Y | 0x8002 | 0x0643 | Y | 0x8002 | 0x0643 | Y | 0x8002 | 0x0643 | Y | 0x8002 | 0x0643 | Y | 0x8002 | 0x0643 | Y | 0x8002 | 0x0643 | Y | 0x8002 | 0x0643 | Y | 0x8002 | 0x0643 | Y | 0x8002 | 0x0643
Rectifier N Communication Failure (N: 1–60) | 0x5122 + (N-1) *16 | MI | 0x00: normal; 0x01: alarm | /Rectifier N communication failure | N | Y | Y | Y | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | N | Y | Y | 0x8002 | 0x0642 | Y | 0x8002 | 0x0642 | Y | 0x8002 0x8003 | 0x0642 0x2260 | Y | 0x8002 0x8003 | 0x0642 0x2260 | Y | 0x8002 | 0x0642 | Y | 0x8002 | 0x0642 | Y | 0x8002 0x8003 | 0x0642 0x2260 | Y | 0x8002 0x8003 | 0x0642 0x2260 | N |  |  | Y | 0x8002 | 0x0642 | Y | 0x8002 | 0x0642 | Y | 0x8002 0x8003 | 0x0642 0x2260 | Y | 0x8002 0x8003 | 0x0642 0x2260 | Y | 0x8002 | 0x0642 | Y | 0x8002 | 0x0642 | Y | 0x8002 0x8003 | 0x0642 0x2260 | Y | 0x8002 | 0x0642 | Y | 0x8002 | 0x0642 | Y | 0x8002 0x8003 | 0x0642 0x2260
Rectifier N Power Failure (N: 1–60) | 0x5123 + (N-1) *16 | MA | 0x00: normal; 0x01: alarm | /Rectifier N power failure | N | Y | Y | Y | Y | Y | N | Y | N | Y | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | Y | 0x8002 | 0x0647 | Y | 0x8002 | 0x0647 | Y | 0x8002 | 0x0647 | N |  |  | Y | 0x8002 | 0x0647 | Y | 0x8002 | 0x0647 | Y | 0x8002 | 0x0647 | N |  |  | N |  |  | Y | 0x8002 | 0x0647 | Y | 0x8002 | 0x0647 | Y | 0x8002 | 0x0647 | Y | 0x8002 | 0x0647 | N |  |  | Y | 0x8002 | 0x0647 | Y | 0x8002 | 0x0647 | N |  |  | Y | 0x8002 | 0x0647
Rectifier N Overvoltage (N: 1–60) | 0x5124 + (N-1) *16 | MA | 0x00: normal; 0x01: alarm | /Rectifier N overvoltage | N | Y | Y | Y | Y | Y | N | Y | N | Y | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | Y | 0x8002 | 0x0648 | Y | 0x8002 | 0x0648 | Y | 0x8002 | 0x0648 | N |  |  | Y | 0x8002 | 0x0648 | Y | 0x8002 | 0x0648 | Y | 0x8002 | 0x0648 | N |  |  | N |  |  | Y | 0x8002 | 0x0648 | Y | 0x8002 | 0x0648 | Y | 0x8002 | 0x0648 | Y | 0x8002 | 0x0648 | N |  |  | Y | 0x8002 | 0x0648 | Y | 0x8002 | 0x0648 | N |  |  | Y | 0x8002 | 0x0648
| Registers Reserved | [10 empty] | N | [11 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Battery High Temperature | 0x5500 | MI | 0x00: normal; 0x01: alarm | Equipment Cabinet power cabinet-battery 1 high temperature, system level, summarization | Y | Y | Y | Y | Y | Y | N | Y | N | Y | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x02BF | Y | 0x8004 | 0x02BF | N |  |  | N |  |  | Y | 0x8004 | 0x02BF | Y | 0x8004 | 0x02BF | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x02BF | Y | 0x8004 | 0x02BF | N |  |  | N |  |  | Y | 0x8004 | 0x02BF | N |  |  | N |  |  | Y | 0x8004 | 0x02BF
Battery Temperature Sensor 1 Fault | 0x5501 | MA | 0x00: normal; 0x01: alarm | Equipment Cabinet power cabinet-battery temperature sensor 1 fault, system level, summarization | Y | Y | Y | Y | Y | Y | N | Y | N | Y | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x2A2C | Y | 0x8004 | 0x2A2C | N |  |  | N |  |  | Y | 0x8004 | 0x2A2C | Y | 0x8004 | 0x2A2C | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x2A2C | Y | 0x8004 | 0x2A2C | N |  |  | N |  |  | Y | 0x8004 | 0x2A2C | N |  |  | N |  |  | Y | 0x8004 | 0x2A2C
BLVD Disconnected | 0x5502 | MA | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when the battery is disconnected. | Y | Y | Y | Y | Y | Y | N | Y | N | Y | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x2777/0x4D35~0x4D37 | Y | 0x8004 | 0x2777/0x4D35~0x4D37 | N |  |  | N |  |  | Y | 0x8004 | 0x2777/0x4D35~0x4D37 | Y | 0x8004 | 0x2777/0x4D35~0x4D37 | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x2777/0x4D35~0x4D37 | Y | 0x8004 | 0x2777/0x4D35~0x4D37 | N |  |  | N |  |  | Y | 0x8004 | 0x2777/0x4D35~0x4D37 | N |  |  | N |  |  | Y | 0x8004 | 0x2777/0x4D35~0x4D37
BLVD Warning | 0x5503 | MA | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when the battery is about to be disconnected. | Y | Y | Y | Y | Y | Y | N | Y | N | Y | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x2775 | Y | 0x8004 | 0x2775 | N |  |  | N |  |  | Y | 0x8004 | 0x2775 | Y | 0x8004 | 0x2775 | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x2775 | Y | 0x8004 | 0x2775 | N |  |  | N |  |  | Y | 0x8004 | 0x2775 | N |  |  | N |  |  | Y | 0x8004 | 0x2775
Battery Forcibly Connection | 0x5504 | MA | 0x00: normal; 0x01: alarm |  | N | Y | Y | Y | Y | Y | N | N | N | Y | N | N | N | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x1057 | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x1057 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x1057 | Y | 0x8004 | 0x1057 | N |  |  | N |  |  | Y | 0x8004 | 0x1057 | N |  |  | N |  |  | Y | 0x8004 | 0x1057
Battery Low Temperature | 0x5505 | MI | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when the low battery temperature alarm is generated. | Y | N | N | N | N | Y | N | Y | N | N | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8004 | 0x02C0 | Y | 0x8004 | 0x02C0 | N |  |  | N |  |  | Y | 0x8004 | 0x02C0 | Y | 0x8004 | 0x02C0 | N |  |  | N |  |  | N |  |  | Y | 0x8004 | 0x02C0 | Y | 0x8004 | 0x02C0 | N |  |  | N |  |  | Y | 0x8004 | 0x02C0 | N |  |  | N |  |  | Y | 0x8004 | 0x02C0
Battery Fuse Blown | 0x5506 | MA | 0x00: normal; 0x01: alarm | Summarizes system-level alarms and reports the alarm when any battery fuse is blown. | Y | N | N | N | N | Y | N | Y | N | N | N | Y | N | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8005 | 0x2A06 | Y | 0x8005 | 0x2A06 | N |  |  | N |  |  | Y | 0x8005 | 0x2A06 | Y | 0x8005 | 0x2A06 | N |  |  | N |  |  | N |  |  | Y | 0x8005 | 0x2A06 | Y | 0x8005 | 0x2A06 | N |  |  | N |  |  | Y | 0x8005 | 0x2A06 | N |  |  | N |  |  | Y | 0x8005 | 0x2A06
Battery Contactor Fault | 0x5507 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | Y | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Battery Reversely Connection | 0x5508 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | Y | N | N | N | N | N | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| Registers Reserved | [10 empty] | N | [11 empty] | N | [8 empty] | N |  |  | N | [8 empty] | N |  |  | N |  |  | N | [14 empty] | N | [8 empty] | N
Battery N Fuse Break/ (N: 1–6) | 0x5520+ (N-1) *16 | CA | 0x00: normal; 0x01: alarm | Battery N fuse blown | N | Y | Y | Y | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8005 | 0x2A06 | Y | 0x8005 | 0x2A06 | N |  |  | N |  |  | Y | 0x8005 | 0x2A06 | Y | 0x8005 | 0x2A06 | N |  |  | N |  |  | N |  |  | Y | 0x8005 | 0x2A06 | Y | 0x8005 | 0x2A06 | N |  |  | N |  |  | Y | 0x8005 | 0x2A06 | N |  |  | N |  |  | Y | 0x8005 | 0x2A06
Battery N Middle Voltage Imbalance (N: 1–6) | 0x5521+ (N-1) *16 | WA | 0x00: normal; 0x01: alarm |  | N | Y | Y | Y | Y | Y | N | N |  | Y |  | Y |  | Y | Y |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8005 | 0x2A0C | Y | 0x8005 | 0x2A0C | N |  |  | N |  |  | Y | 0x8005 | 0x2A0C | Y | 0x8005 | 0x2A0C | N |  |  | N |  |  | N |  |  | Y | 0x8005 | 0x2A0C | Y | 0x8005 | 0x2A0C | N |  |  | N |  |  | Y | 0x8005 | 0x2A0C | N |  |  | N |  |  | Y | 0x8005 | 0x2A0C
| Registers Reserved | [20 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Return Air Temperature Sensor 1 Fault | 0x5700 | MA | 0x00: normal; 0x01: alarm | Equipment Cabinet-(power) cabinet interior return air vent sensor fault | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x800B | 0x26E0 | N |  |  | N |  |  | N |  |  | Y | 0x800B | 0x26E0 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x800B | 0x26E0 | Y | 0x800B | 0x26E0 | N |  |  | N |  |  | Y | 0x800B | 0x26E0 | N |  |  | N |  |  | Y | 0x800B | 0x26E0
Outdoor Ambient Temperature Sensor Fault | 0x5701 | CA | 0x00: normal; 0x01: alarm | Equipment Cabinet/(power) cabinet exterior ambient sensor fault | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x800B | 0x26E1 | N |  |  | N |  |  | N |  |  | Y | 0x800B | 0x26E1 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x800B | 0x26E1 | Y | 0x800B | 0x26E1 | N |  |  | N |  |  | Y | 0x800B | 0x26E1 | N |  |  | N |  |  | Y | 0x800B | 0x26E1
| Registers Reserved | [22 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N | [5 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Fan 1 Fault | 0x5720 | MA | 0x00: normal; 0x01: alarm | Equipment Cabinet | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x800C | 0x26E6 | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x26E6 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x26E6 | Y | 0x800C | 0x26E6 | N |  |  | N |  |  | Y | 0x800C | 0x26E6 | N |  |  | N |  |  | Y | 0x800C | 0x26E6
Fan 2 Fault | 0x5721 | MA | 0x00: normal; 0x01: alarm | Equipment Cabinet | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x800C | 0x26E7 | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x26E7 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x26E7 | Y | 0x800C | 0x26E7 | N |  |  | N |  |  | Y | 0x800C | 0x26E7 | N |  |  | N |  |  | Y | 0x800C | 0x26E7
Fan 3 Fault | 0x5722 | MA | 0x00: normal; 0x01: alarm | Equipment Cabinet | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x800C | 0x26E8 | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x26E8 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x26E8 | Y | 0x800C | 0x26E8 | N |  |  | N |  |  | Y | 0x800C | 0x26E8 | N |  |  | N |  |  | Y | 0x800C | 0x26E8
Fan 4 Fault | 0x5723 | MA | 0x00: normal; 0x01: alarm | Equipment Cabinet | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x800C | 0x26E9 | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x26E9 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x800C | 0x26E9 | Y | 0x800C | 0x26E9 | N |  |  | N |  |  | Y | 0x800C | 0x26E9 | N |  |  | N |  |  | Y | 0x800C | 0x26E9
| Registers Reserved | [10 empty] | N | [11 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Air Conditioner 1 Internal Fan Fault | 0x5740 | MA | 0x00: normal; 0x01: alarm | Equipment Cabinet | N | Y | Y | Y | Y | Y | N | N |  | Y |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8009 | 0x2486 | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x2486 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x2486 | Y | 0x8009 | 0x2486 | N |  |  | N |  |  | Y | 0x8009 | 0x2486 | N |  |  | N |  |  | Y | 0x8009 | 0x2486
Air Conditioner 1 External Fan Fault | 0x5741 | MA | 0x00: normal; 0x01: alarm | Equipment Cabinet | N | Y | Y | Y | Y | Y | N | N |  | Y |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8009 | 0x2487 | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x2487 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x2487 | Y | 0x8009 | 0x2487 | N |  |  | N |  |  | Y | 0x8009 | 0x2487 | N |  |  | N |  |  | Y | 0x8009 | 0x2487
Air Conditioner 1 Compressor Fault | 0x5742 | MA | 0x00: normal; 0x01: alarm | Equipment Cabinet | N | Y | Y | Y | Y | Y | N | N |  | Y |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8009 | 0x2489 | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x2489 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x2489 | Y | 0x8009 | 0x2489 | N |  |  | N |  |  | Y | 0x8009 | 0x2489 | N |  |  | N |  |  | Y | 0x8009 | 0x2489
Air Conditioner 1 Evaporator Frozen | 0x5743 | MA | 0x00: normal; 0x01: alarm | Equipment Cabinet | N | Y | Y | Y | Y | Y | N | N |  | Y |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8009 | 0x2494 | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x2494 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x2494 | Y | 0x8009 | 0x2494 | N |  |  | N |  |  | Y | 0x8009 | 0x2494 | N |  |  | N |  |  | Y | 0x8009 | 0x2494
Air Conditioner 1 Frequent High Pressure | 0x5744 | MA | 0x00: normal; 0x01: alarm | Equipment Cabinet | N | Y | Y | Y | Y | Y | N | N |  | Y |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8009 | 0x2495 | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x2495 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x2495 | Y | 0x8009 | 0x2495 | N |  |  | N |  |  | Y | 0x8009 | 0x2495 | N |  |  | N |  |  | Y | 0x8009 | 0x2495
Air Conditioner 1 Communication Failure | 0x5745 | MA | 0x00: normal; 0x01: alarm | Equipment Cabinet | N | Y | Y | Y | Y | Y | N | N |  | Y |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8009 | 0x248A | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x248A | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8009 | 0x248A | Y | 0x8009 | 0x248A | N |  |  | N |  |  | Y | 0x8009 | 0x248A | N |  |  | N |  |  | Y | 0x8009 | 0x248A
| Registers(0x5746~0x575F) Reserved for the Air Conditioner |  |  |  | N | Y | Y | Y | Y | Y | N | N |  |  |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Air Conditioner 2 Internal Fan Fault | 0x5760 | MA | 0x00: normal; 0x01: alarm | Battery Cabinet | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x2983 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2983 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2983 | Y | 0x8022 | 0x2983 | N |  |  | N |  |  | Y | 0x8022 | 0x2983 | N |  |  | N |  |  | Y | 0x8022 | 0x2983
Air Conditioner 2 External Fan Fault | 0x5761 | MA | 0x00: normal; 0x01: alarm | Battery Cabinet | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x2986 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2986 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2986 | Y | 0x8022 | 0x2986 | N |  |  | N |  |  | Y | 0x8022 | 0x2986 | N |  |  | N |  |  | Y | 0x8022 | 0x2986
Air Conditioner 2 Compressor Fault | 0x5762 | MA | 0x00: normal; 0x01: alarm | Battery Cabinet | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x2987 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2987 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2987 | Y | 0x8022 | 0x2987 | N |  |  | N |  |  | Y | 0x8022 | 0x2987 | N |  |  | N |  |  | Y | 0x8022 | 0x2987
Air Conditioner 2 Evaporator Frozen | 0x5763 | MA | 0x00: normal; 0x01: alarm | Battery Cabinet | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x2988 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2988 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2988 | Y | 0x8022 | 0x2988 | N |  |  | N |  |  | Y | 0x8022 | 0x2988 | N |  |  | N |  |  | Y | 0x8022 | 0x2988
Air Conditioner 2 Frequent High Pressure | 0x5764 | MA | 0x00: normal; 0x01: alarm | Battery Cabinet | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x2984 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2984 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2984 | Y | 0x8022 | 0x2984 | N |  |  | N |  |  | Y | 0x8022 | 0x2984 | N |  |  | N |  |  | Y | 0x8022 | 0x2984
Air Conditioner 2 Communication Failure | 0x5765 | MA | 0x00: normal; 0x01: alarm | Battery Cabinet | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x2985 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2985 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2985 | Y | 0x8022 | 0x2985 | N |  |  | N |  |  | Y | 0x8022 | 0x2985 | N |  |  | N |  |  | Y | 0x8022 | 0x2985
Fan 1 Fault | 0x5766 | MA | 0x00: normal; 0x01: alarm | Battery Cabinet | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x2975 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2975 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2975 | Y | 0x8022 | 0x2975 | N |  |  | N |  |  | Y | 0x8022 | 0x2975 | N |  |  | N |  |  | Y | 0x8022 | 0x2975
Fan 2 Fault | 0x5767 | MA | 0x00: normal; 0x01: alarm | Battery Cabinet | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x2976 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2976 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2976 | Y | 0x8022 | 0x2976 | N |  |  | N |  |  | Y | 0x8022 | 0x2976 | N |  |  | N |  |  | Y | 0x8022 | 0x2976
Fan 3 Fault | 0x5768 | MA | 0x00: normal; 0x01: alarm | Battery Cabinet | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x2977 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2977 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2977 | Y | 0x8022 | 0x2977 | N |  |  | N |  |  | Y | 0x8022 | 0x2977 | N |  |  | N |  |  | Y | 0x8022 | 0x2977
Fan 4 Fault | 0x5769 | MA | 0x00: normal; 0x01: alarm | Battery Cabinet | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x2978 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2978 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2978 | Y | 0x8022 | 0x2978 | N |  |  | N |  |  | Y | 0x8022 | 0x2978 | N |  |  | N |  |  | Y | 0x8022 | 0x2978
High Battery Area Temperature | 0x576A | MI | 0x00: normal; 0x01: alarm | Battery Cabinet | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x297C | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x297C | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x297C | Y | 0x8022 | 0x297C | N |  |  | N |  |  | Y | 0x8022 | 0x297C | N |  |  | N |  |  | Y | 0x8022 | 0x297C
Battery Area Temperature Sensor Fault | 0x576B | MA | 0x00: normal; 0x01: alarm | Battery Cabinet | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x298C | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x298C | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x298C | Y | 0x8022 | 0x298C | N |  |  | N |  |  | Y | 0x8022 | 0x298C | N |  |  | N |  |  | Y | 0x8022 | 0x298C
Battery 2 High Temperature | 0x576C | MI | 0x00: normal; 0x01: alarm | Battery Cabinet | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x2972 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2972 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2972 | Y | 0x8022 | 0x2972 | N |  |  | N |  |  | Y | 0x8022 | 0x2972 | N |  |  | N |  |  | Y | 0x8022 | 0x2972
Battery Temperature Sensor 2 Fault | 0x576D | MA | 0x00: normal; 0x01: alarm | Battery Cabinet | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x2973 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2973 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2973 | Y | 0x8022 | 0x2973 | N |  |  | N |  |  | Y | 0x8022 | 0x2973 | N |  |  | N |  |  | Y | 0x8022 | 0x2973
Return Air Temperature Sensor 2 Fault | 0x576E | CA | 0x00: normal; 0x01: alarm | Battery Cabinet | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x297D | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x297D | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x297D | Y | 0x8022 | 0x297D | N |  |  | N |  |  | Y | 0x8022 | 0x297D | N |  |  | N |  |  | Y | 0x8022 | 0x297D
Door Alarm | 0x576F | MA | 0x00: normal; 0x01: alarm | Battery Cabinet | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x2989 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2989 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2989 | Y | 0x8022 | 0x2989 | N |  |  | N |  |  | Y | 0x8022 | 0x2989 | N |  |  | N |  |  | Y | 0x8022 | 0x2989
Battery Cabinet Communication Failure | 0x5772 | MA | 0x00: normal; 0x01: alarm | Battery Cabinet | N | Y | Y | Y | Y | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8022 | 0x2971 | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2971 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8022 | 0x2971 | Y | 0x8022 | 0x2971 | N |  |  | N |  |  | Y | 0x8022 | 0x2971 | N |  |  | N |  |  | Y | 0x8022 | 0x2971
| Registers(0x5773~0x577F) Reserved for the TCUX |  |  |  | N | Y | Y | Y | Y | Y | N | N |  |  |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| Registers Reserved | [10 empty] | N | [11 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG 1 Interface Board Hardware Fault | 0x5820 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG 1 Interface Board Communication Failure | 0x5821 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG 1 Communication Failure | 0x5822 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG 2 Interface Board Hardware Fault | 0x5823 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG 2 Interface Board Communication Failure | 0x5824 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG 2 Communication Failure | 0x5825 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| Registers Reserved | [10 empty] | N | [9 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Start Failure (N:1–2) | 0x5830+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Stop Failure | 0x 5831+(N-1)*64 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Low Battery Voltage | 0x 5832+(N-1)*64 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Low Oil Pressure | 0x 5833+(N-1)*64 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Low Oil Pressure Protection | 0x 5834+(N-1)*64 | CA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N High Water Temperature | 0x 5835+(N-1)*64 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N High Water Temperature Protection | 0x 5836+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Overload Protection | 0x 5837+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Output Overvoltage Protection | 0x 5838+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Output Undervoltage Protection | 0x 5839+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Overspeed Protection | 0x 583A+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Battery Voltage Abnormal | 0x 583B+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N First Maintenance Reminder | 0x 583C+(N-1)*64 | WA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Routine Maintenance Reminder | 0x 583D+(N-1)*64 | WA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Routine Maintenance Period Setting Error | 0x 583E+(N-1)*64 | WA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Timed Maintenance Reminder | 0x 583F+(N-1)*64 | WA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Door Open | 0x5840+(N-1)*64 | WA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Low Water Level | 0x 5841+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Abnormal Stop | 0x 5842+(N-1)*64 | WA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Abnormal Start | 0x 5843+(N-1)*64 | WA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N GCB Fault | 0x 5844+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Running | 0x 5845+(N-1)*64 | WA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Motor Charger Fault | 0x 5846+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Low Auxiliary Sump Oil Level | 0x 5847+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Oil Pressure Sensor Failure | 0x 5848+(N-1)*64 | WA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Water Temperature Sensor Failure | 0x 5849+(N-1)*64 | WA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Generator Voltage Not Balance | 0x 584A+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Generator Over Frequency | 0x 584B+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Generator Under Frequency | 0x 584C+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Generator Current Not Balance | 0x 584D+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Charge Failure | 0x 584E+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Speed Sensor Failure | 0x 584F+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Shortcut Protection | 0x5850+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N IDMT Protection | 0x 5851+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N MCB Failure | 0x 5852+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Lost Phase Protection | 0x 5853+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Emergency Stop | 0x 5854+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Fault | 0x 5855+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DG N Nonautomatic Mode Alarm | 0x 5856+(N-1)*64 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSU Lost | 0x5900 | WA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | Y |  | Y |  | Y | Y | Y | Y | N | Y | N |  |  | N |  |  | Y | 0x8011 | 0x2296 | Y | 0x8011 | 0x2296 | N |  |  | N |  |  | Y | 0x8011 | 0x2296 | Y | 0x8011 | 0x2296 | N |  |  | N |  |  | N |  |  | Y | 0x8011 | 0x2296 | Y | 0x8011 | 0x2296 | N |  |  | N |  |  | Y | 0x8011 | 0x2296 | N |  |  | N |  |  | Y | 0x8011 | 0x2296
SSU1–N (N=60) Fault | 0x5901+(N-1)*16 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | Y |  | Y [sequence]Insubrack first, Outsubrack later |  | Y [sequence]Insubrack first, Outsubrack later | Y [sequence]Insubrack first, Outsubrack later | Y [sequence]Insubrack first, Outsubrack later | Y [sequence]Insubrack first, Outsubrack later | N | Y [sequence]Insubrack first, Outsubrack later | N |  |  | N |  |  | Y [sequence]Insubrack first, Outsubrack later | 0x8012 | 0x0672 | Y [sequence]Insubrack first, Outsubrack later | 0x8012 | 0x0672 | N |  |  | N |  |  | Y [sequence]Insubrack first, Outsubrack later | 0x8012 | 0x0672 | Y [sequence]Insubrack first, Outsubrack later | 0x8012 | 0x0672 | Y [sequence]Insubrack first, Outsubrack later | 0x8012 | 0x0672 | N |  |  | N |  |  | Y [sequence]Insubrack first, Outsubrack later | 0x8012 | 0x0672 | Y [sequence]Insubrack first, Outsubrack later | 0x8012 | 0x0672 | N |  |  | N |  |  | Y [sequence]Insubrack first, Outsubrack later | 0x8012 | 0x0672 | N |  |  | N |  |  | Y [sequence]Insubrack first, Outsubrack later | 0x8012 | 0x0672
SSU1–N (N=60) Communication Failure | 0x5902+(N-1)*16 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | Y |  | Y [sequence]Insubrack first, Outsubrack later |  | Y [sequence]Insubrack first, Outsubrack later | Y [sequence]Insubrack first, Outsubrack later | Y [sequence]Insubrack first, Outsubrack later | Y [sequence]Insubrack first, Outsubrack later | N | Y [sequence]Insubrack first, Outsubrack later | N |  |  | N |  |  | Y [sequence]Insubrack first, Outsubrack later | 0x8012 0x8011 | 0x0674 0x2294 | Y [sequence]Insubrack first, Outsubrack later | 0x8012 0x8011 | 0x0674 0x2294 | N |  |  | N |  |  | Y [sequence]Insubrack first, Outsubrack later | 0x8012 0x8011 | 0x0674 0x2294 | Y [sequence]Insubrack first, Outsubrack later | 0x8012 0x8011 | 0x0674 0x2294 | Y [sequence]Insubrack first, Outsubrack later | 0x8012 0x8011 | 0x0674 0x2294 | N |  |  | N |  |  | Y [sequence]Insubrack first, Outsubrack later | 0x8012 0x8011 | 0x0674 0x2294 | Y [sequence]Insubrack first, Outsubrack later | 0x8012 0x8011 | 0x0674 0x2294 | N |  |  | N |  |  | Y [sequence]Insubrack first, Outsubrack later | 0x8012 0x8011 | 0x0674 0x2294 | N |  |  | N |  |  | Y [sequence]Insubrack first, Outsubrack later | 0x8012 0x8011 | 0x0674 0x2294
PV1–N (N=60) Array Fault | 0x5903+(N-1)*16 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | Y |  | N |  | Y | N | Y | Y | N | Y | N |  |  | N |  |  | Y | 0x8012 | 0x2292 | N | 0x8012 | 0x2292 | N |  |  | N |  |  | Y | 0x8012 | 0x2292 | N | 0x8012 | 0x2292 | Y | 0x8012 | 0x2292 | N |  |  | N |  |  | Y | 0x8012 | 0x2292 | Y | 0x8012 | 0x2292 | N |  |  | N |  |  | Y | 0x8012 | 0x2292 | N |  |  | N |  |  | Y | 0x8012 | 0x2292
SSU1–N (N=60) Protection | 0x5904+(N-1)*16 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | Y |  | Y [sequence]Insubrack first, Outsubrack later |  | Y [sequence]Insubrack first, Outsubrack later | Y [sequence]Insubrack first, Outsubrack later | Y [sequence]Insubrack first, Outsubrack later | Y [sequence]Insubrack first, Outsubrack later | N | Y [sequence]Insubrack first, Outsubrack later | N |  |  | N |  |  | Y [sequence]Insubrack first, Outsubrack later | 0x8012 | 0x0675 | Y [sequence]Insubrack first, Outsubrack later | 0x8012 | 0x0675 | N |  |  | N |  |  | Y [sequence]Insubrack first, Outsubrack later | 0x8012 | 0x0675 | Y [sequence]Insubrack first, Outsubrack later | 0x8012 | 0x0675 | Y [sequence]Insubrack first, Outsubrack later | 0x8012 | 0x0675 | N |  |  | N |  |  | Y [sequence]Insubrack first, Outsubrack later | 0x8012 | 0x0675 | Y [sequence]Insubrack first, Outsubrack later | 0x8012 | 0x0675 | N |  |  | N |  |  | Y [sequence]Insubrack first, Outsubrack later | 0x8012 | 0x0675 | N |  |  | N |  |  | Y [sequence]Insubrack first, Outsubrack later | 0x8012 | 0x0675
| Registers Reserved(0x5CB5~0x5FFF)for other SSU | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
System Manual Control | 0x6000 | WA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DCDC N Fault (N: 1–14) | 0x6001 + (N-1) *8 | MA | 0x00: normal; 0x01: alarm | DCDC N fault | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DCDC N Protection (N: 1–14) | 0x6002 + (N-1) *8 | MI | 0x00: normal; 0x01: alarm | DCDC N protection | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DCDC N Communication Failure (N: 1–14) | 0x6003 + (N-1) *8 | MI | 0x00: normal; 0x01: alarm | DCDC N communication failure | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DCDC N Overvoltage (N: 1–14) | 0x6004 + (N-1) *8 | MA | 0x00: normal; 0x01: alarm | DCDC N overvoltage | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| reserve (0x6070~0x6078) | [22 empty] | N | [8 empty] | N |  |  | N | [8 empty] | N |  |  | N |  |  | N | [14 empty] | N | [8 empty] | N
AAU1 Disconnecting | 0x6079 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU1 Disconnected | 0x607A | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU1 Fuse Break | 0x607B | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Power Unit 1 Module Missing | 0x607C | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
57V DC Over Voltage | 0x607D | MA | 0x00: normal; 0x01: alarm | [8 empty] | Y | [9 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
57V DC Under Voltage | 0x607E | MA | 0x00: normal; 0x01: alarm | [8 empty] | Y | [9 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| reserve (0x607F~0x6080) | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU2 Disconnecting | 0x6081 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU2 Disconnected | 0x6082 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU2 Fuse Break | 0x6083 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Power Unit 2 Module Missing | 0x6084 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
57V DC Over Voltage | 0x6085 | MA | 0x00: normal; 0x01: alarm | [8 empty] | Y | [9 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
57V DC Under Voltage | 0x6086 | MA | 0x00: normal; 0x01: alarm | [8 empty] | Y | [9 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| reserve (0x6087~0x6088) | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU3 Disconnecting | 0x6089 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU3 Disconnected | 0x608A | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AAU3 Fuse Break | 0x608B | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Power Unit 3 Module Missing | 0x608C | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | N | Y |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
57V DC Over Voltage | 0x608D | MA | 0x00: normal; 0x01: alarm | [8 empty] | Y | [9 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
57V DC Under Voltage | 0x608E | MA | 0x00: normal; 0x01: alarm | [8 empty] | Y | [9 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| reserve (0x608F~0x6090) | [20 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| reserve (0x6091~0x6098) | [20 empty] | N |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Rectifier M# in rectifier cabinet N# (N: 1–8; M: 1–60) | 0x7000 + (N-1)*60 + (M-1) | MA | 0x00-Rectifier normal 0x01-Rectifier fault 0x02-Rectifier protection 0x03-Rectifier communication failure 0x04-Rectifier power failure 0x05-Rectifier overvoltage |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9004 | 0x1550~0x158B | N |  |  | N |  |  | N |  |  | Y | 0x9004 | 0x1550~0x158B | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9004 | 0x1550~0x158B | Y | 0x9004 | 0x1550~0x158B | N |  |  | N |  |  | Y | 0x9004 | 0x1550~0x158B | N |  |  | N |  |  | Y | 0x9004 | 0x1550~0x158B
| 0x71E0–0x71EF reserved | [10 empty] | N | [11 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Rectifier M# in combined cabinet N# (N: 1–8; M: 1–60) | 0x71F0+(N-1)*60 + (M-1) |  | 0x00-Rectifier normal 0x01-Rectifier fault 0x02-Rectifier protection 0x03-Rectifier communication failure 0x04-Rectifier power failure 0x05-Rectifier overvoltage |  | Y | N | N | N | N | Y | Y | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9003 | 0x1550~0x158B | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x1550~0x158B | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x1550~0x158B | Y | 0x9003 | 0x1550~0x158B | N |  |  | N |  |  | Y | 0x9003 | 0x1550~0x158B | N |  |  | N |  |  | Y | 0x9003 | 0x1550~0x158B
| (0x73D0–0x76FF) reserved | [10 empty] | N | [11 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DC surge protection alarm for combined cabinet N# N: 1–8 | 0x7700+ (N-1)*54 | MA | 0x00: normal 0x01: alarm |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9003 | 0x1516 | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x1516 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x1516 | Y | 0x9003 | 0x1516 | N |  |  | N |  |  | Y | 0x9003 | 0x1516 | N |  |  | N |  |  | Y | 0x9003 | 0x1516
DC voltage alarm for combined cabinet N# N: 1–8 | 0x7701+ (N-1)*54 | MA | 0x00: normal 0x01: overvoltage 0x02: undervoltage |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9003 | 0x1517 | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x1517 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x1517 | Y | 0x9003 | 0x1517 | N |  |  | N |  |  | Y | 0x9003 | 0x1517 | N |  |  | N |  |  | Y | 0x9003 | 0x1517
Load fuse M in combined cabinet N# N: 1–8; M: 1–42 | 0x7702+ (N-1)*54 + (M-1) | MA | 0x00: normal 0x01: alarm |  | Y | N | N | N | N | Y | Y | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9003 | 0x1518~0x1541 | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x1518~0x1541 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x1518~0x1541 | Y | 0x9003 | 0x1518~0x1541 | N |  |  | N |  |  | Y | 0x9003 | 0x1518~0x1541 | N |  |  | N |  |  | Y | 0x9003 | 0x1518~0x1541
Battery fuse M in combined cabinet N# N: 1–8; M: 1–10 | 0x7702+ (N-1)*54 + (M-1)+42 | MA | 0x00: normal 0x01: alarm |  | Y | N | N | N | N | Y | Y | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9003 | 0x1542~0x154B | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x1542~0x154B | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9003 | 0x1542~0x154B | Y | 0x9003 | 0x1542~0x154B | N |  |  | N |  |  | Y | 0x9003 | 0x1542~0x154B | N |  |  | N |  |  | Y | 0x9003 | 0x1542~0x154B
| Reserved (0x78B0–0x78FF) |  |  |  | Y |  |  |  |  | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AC surge protection for combined cabinet N# N: 1–8 | 0x7900+ (N-1)*8 | MA | 0x00: normal 0x01: alarm |  | Y | N | N | N | N | Y | Y | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x1827 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1827 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1827 | Y | 0x8231 | 0x1827 | N |  |  | N |  |  | Y | 0x8231 | 0x1827 | N |  |  | N |  |  | Y | 0x8231 | 0x1827
AC power failure for combined cabinet N# N: 1–8 | 0x7901+ (N-1)*8 | MA | 0x00: normal 0x01: alarm | The AC alarm is comprehensive information. If multiple AC inputs exist, reports the alarm when any input generates an alarm. | Y | N | N | N | N | Y | Y | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x1828 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1828 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1828 | Y | 0x8231 | 0x1828 | N |  |  | N |  |  | Y | 0x8231 | 0x1828 | N |  |  | N |  |  | Y | 0x8231 | 0x1828
AC L1/L1L2 alarm for combined cabinet N# N: 1–8 | 0x7902+ (N-1)*8 | MI | 0x00: L1 normal 0x01: L1 overvoltage 0x02: L1 undervoltage 0x03: L1 open-phase | The AC alarm is comprehensive information. If multiple AC inputs exist, reports the alarm when any input generates an alarm. | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x1829 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1829 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1829 | Y | 0x8231 | 0x1829 | N |  |  | N |  |  | Y | 0x8231 | 0x1829 | N |  |  | N |  |  | Y | 0x8231 | 0x1829
AC L2/L2L3 alarm for combined cabinet N# N: 1–8 | 0x7903+ (N-1)*8 | MI | 0x00: L1 normal 0x01: L1 overvoltage 0x02: L1 undervoltage 0x03: L1 open-phase | The AC alarm is comprehensive information. If multiple AC inputs exist, reports the alarm when any input generates an alarm. | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x182A | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x182A | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x182A | Y | 0x8231 | 0x182A | N |  |  | N |  |  | Y | 0x8231 | 0x182A | N |  |  | N |  |  | Y | 0x8231 | 0x182A
AC L3/L3L1 alarm for combined cabinet N# N: 1–8 | 0x7904+ (N-1)*8 | MI | 0x00: L1 normal 0x01: L1 overvoltage 0x02: L1 undervoltage 0x03: L1 open-phase | The AC alarm is comprehensive information. If multiple AC inputs exist, reports the alarm when any input generates an alarm. | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x182B | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x182B | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x182B | Y | 0x8231 | 0x182B | N |  |  | N |  |  | Y | 0x8231 | 0x182B | N |  |  | N |  |  | Y | 0x8231 | 0x182B
AC frequency alarm for combined cabinet N# N: 1–8 | 0x7905+ (N-1)*8 | MI | 0x00: normal 0x01: high frequency 0x02: low frequency | The AC alarm is comprehensive information. If multiple AC inputs exist, reports the alarm when any input generates an alarm. | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x182C | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x182C | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x182C | Y | 0x8231 | 0x182C | N |  |  | N |  |  | Y | 0x8231 | 0x182C | N |  |  | N |  |  | Y | 0x8231 | 0x182C
| Reserve two registers for each cabinet. |  |  |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bus Bar Overvoltage for combined cabinet N# N: 1–8 | 0x7940+ (N-1)*16 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bus Bar Undervoltage for combined cabinet N# N: 1–8 | 0x7941+ (N-1)*16 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Communication Failure for combined cabinet N# N: 1–8 | 0x7942+ (N-1)*16 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
LLVD Disconnected for combined cabinet N# N: 1–8 | 0x7943+ (N-1)*16 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
BLVD Disconnected for combined cabinet N# N: 1–8 | 0x7944+ (N-1)*16 | CA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AC Overvoltage for combined cabinet N# N: 1–8 | 0x7945+ (N-1)*16 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AC Undervoltage for combined cabinet N# N: 1–8 | 0x7946+ (N-1)*16 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Door Open Alarm for combined cabinet N# N: 1–8 | 0x7947+ (N-1)*16 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Smoke Alarm for combined cabinet N# N: 1–8 | 0x7948+ (N-1)*16 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Water Alarm for combined cabinet N# N: 1–8 | 0x7949+ (N-1)*16 | MA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Ambient High Temperature for combined cabinet N# N: 1–8 | 0x794A+ (N-1)*16 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Ambient Low Temperature for combined cabinet N# N: 1–8 | 0x794B+ (N-1)*16 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Ambient High Humidity for combined cabinet N# N: 1–8 | 0x794C+ (N-1)*16 | WA | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Battery 1 Charge Overcurrent for combined cabinet N# N: 1–8 | 0x794D+ (N-1)*16 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Battery 2 Charge Overcurrent for combined cabinet N# N: 1–8 | 0x794E+ (N-1)*16 | MI | 0x00: normal; 0x01: alarm |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| Reserve one registers for each cabinet. |  |  |  | N | N | N | N | N | N | Y | N |  | N |  | N |  | N | N |  | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| 0x79A0–0x7AFF reserved | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AC surge protection for AC cabinet N# N: 1–8 | 0x7B00+(N-1)*12 | MA | 0x00: normal 0x01: alarm |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9001 | 0x1018 | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1018 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1018 | Y | 0x9001 | 0x1018 | N |  |  | N |  |  | Y | 0x9001 | 0x1018 | N |  |  | N |  |  | Y | 0x9001 | 0x1018
AC power failure of the first route in AC cabinet N# N: 1–8 | 0x7B01+(N-1)*12 | MA | 0x00: normal 0x01: alarm |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9001 | 0x1019 | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1019 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1019 | Y | 0x9001 | 0x1019 | N |  |  | N |  |  | Y | 0x9001 | 0x1019 | N |  |  | N |  |  | Y | 0x9001 | 0x1019
AC L1/L1L2 alarm for the first route in AC cabinet N# N:1–8 | 0x7B02+(N-1)*12 | MI | 0x00: L1 normal 0x01: L1 overvoltage 0x02: L1 undervoltage 0x03: L1 open-phase |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9001 | 0x1020 | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1020 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1020 | Y | 0x9001 | 0x1020 | N |  |  | N |  |  | Y | 0x9001 | 0x1020 | N |  |  | N |  |  | Y | 0x9001 | 0x1020
AC L2/L2L3 alarm for the first route in AC cabinet N# N:1–8 | 0x7B03+(N-1)*12 | MI | 0x00: L1 normal 0x01: L1 overvoltage 0x02: L1 undervoltage 0x03: L1 open-phase |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9001 | 0x1021 | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1021 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1021 | Y | 0x9001 | 0x1021 | N |  |  | N |  |  | Y | 0x9001 | 0x1021 | N |  |  | N |  |  | Y | 0x9001 | 0x1021
AC L3/L3L1 alarm for the first route in AC cabinet N# N: 1–8 | 0x7B04+(N-1)*12 | MI | 0x00: L1 normal 0x01: L1 overvoltage 0x02: L1 undervoltage 0x03: L1 open-phase |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9001 | 0x1022 | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1022 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1022 | Y | 0x9001 | 0x1022 | N |  |  | N |  |  | Y | 0x9001 | 0x1022 | N |  |  | N |  |  | Y | 0x9001 | 0x1022
AC frequency alarm for the first route in AC cabinet N# N: 1–8 | 0x7B05+(N-1)*12 | MI | 0x00-normal 0x01: high frequency 0x02: low frequency |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9001 | 0x1023 | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1023 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1023 | Y | 0x9001 | 0x1023 | N |  |  | N |  |  | Y | 0x9001 | 0x1023 | N |  |  | N |  |  | Y | 0x9001 | 0x1023
AC power failure of the second route in AC cabinet N# N: 1–8 | 0x7B06+(N-1)*12 | MA | 0x00: normal 0x01: alarm |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9001 | 0x1024 | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1024 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1024 | Y | 0x9001 | 0x1024 | N |  |  | N |  |  | Y | 0x9001 | 0x1024 | N |  |  | N |  |  | Y | 0x9001 | 0x1024
AC L1/L1L2 alarm for the second route in AC cabinet N# N: 1–8 | 0x7B07+(N-1)*12 | MI | 0x00: L1 normal 0x01: L1 overvoltage 0x02: L1 undervoltage 0x03: L1 open-phase |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9001 | 0x1025 | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1025 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1025 | Y | 0x9001 | 0x1025 | N |  |  | N |  |  | Y | 0x9001 | 0x1025 | N |  |  | N |  |  | Y | 0x9001 | 0x1025
AC L2/L2L3 alarm for the second route in AC cabinet N# N: 1–8 | 0x7B08+(N-1)*12 | MI | 0x00: L1 normal 0x01: L1 overvoltage 0x02: L1 undervoltage 0x03: L1 open-phase |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9001 | 0x1026 | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1026 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1026 | Y | 0x9001 | 0x1026 | N |  |  | N |  |  | Y | 0x9001 | 0x1026 | N |  |  | N |  |  | Y | 0x9001 | 0x1026
AC L3/L3L1 alarm for the second route in AC cabinet N# N: 1–8 | 0x7B09+(N-1)*12 | MI | 0x00: L1 normal 0x01: L1 overvoltage 0x02: L1 undervoltage 0x03: L1 open-phase |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9001 | 0x1027 | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1027 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1027 | Y | 0x9001 | 0x1027 | N |  |  | N |  |  | Y | 0x9001 | 0x1027 | N |  |  | N |  |  | Y | 0x9001 | 0x1027
AC frequency alarm for the second route in AC cabinet N# N: 1–8 | 0x7B0A+(N-1)*12 | MI | 0x00: normal 0x01: high frequency 0x02: low frequency |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x9001 | 0x1028 | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1028 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x9001 | 0x1028 | Y | 0x9001 | 0x1028 | N |  |  | N |  |  | Y | 0x9001 | 0x1028 | N |  |  | N |  |  | Y | 0x9001 | 0x1028
| Reserve one register for each cabinet. |  |  |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| 0x7B60–0x7B6F reserved | [12 empty] | N | [9 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
AC surge protection for rectifier cabinet N# N: 1–8 | 0x7B70+ (N-1)*8 | MA | 0x00: normal 0x01: alarm |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x1827 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1827 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1827 | Y | 0x8231 | 0x1827 | N |  |  | N |  |  | Y | 0x8231 | 0x1827 | N |  |  | N |  |  | Y | 0x8231 | 0x1827
AC power failure for rectifier cabinet N# N: 1–8 | 0x7B71+ (N-1)*8 | MA | 0x00: normal 0x01: alarm |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x1828 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1828 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1828 | Y | 0x8231 | 0x1828 | N |  |  | N |  |  | Y | 0x8231 | 0x1828 | N |  |  | N |  |  | Y | 0x8231 | 0x1828
AC L1/L1L2 alarm for rectifier cabinet N# N: 1–8 | 0x7B72+ (N-1)*8 | MI | 0x00: L1 normal 0x01: L1 overvoltage 0x02: L1 undervoltage 0x03: L1 open-phase |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x1829 | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1829 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x1829 | Y | 0x8231 | 0x1829 | N |  |  | N |  |  | Y | 0x8231 | 0x1829 | N |  |  | N |  |  | Y | 0x8231 | 0x1829
AC L2/L2L3 alarm for rectifier cabinet N# N: 1–8 | 0x7B73+ (N-1)*8 | MI | 0x00: L1 normal 0x01: L1 overvoltage 0x02: L1 undervoltage 0x03: L1 open-phase |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x182A | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x182A | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x182A | Y | 0x8231 | 0x182A | N |  |  | N |  |  | Y | 0x8231 | 0x182A | N |  |  | N |  |  | Y | 0x8231 | 0x182A
AC L3/L3L1 alarm for rectifier cabinet N# N: 1–8 | 0x7B74+ (N-1)*8 | MI | 0x00: L1 normal 0x01: L1 overvoltage 0x02: L1 undervoltage 0x03: L1 open-phase |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x182B | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x182B | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x182B | Y | 0x8231 | 0x182B | N |  |  | N |  |  | Y | 0x8231 | 0x182B | N |  |  | N |  |  | Y | 0x8231 | 0x182B
AC frequency alarm for rectifier cabinet N# N: 1–8 | 0x7B75+ (N-1)*8 | MI | 0x00: normal 0x01: high frequency 0x02: low frequency |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x8231 | 0x182C | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x182C | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x8231 | 0x182C | Y | 0x8231 | 0x182C | N |  |  | N |  |  | Y | 0x8231 | 0x182C | N |  |  | N |  |  | Y | 0x8231 | 0x182C
| Reserve two registers for each cabinet. |  |  |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| 0x7BB0–0x7BBF reserved | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Surge protection alarm for DC cabinet N# N: 1–14 | 0x7BC0+(N-1)*138 | MA | 0x00: normal 0x01: alarm |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x193F | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x193F | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x193F | Y | 0x826A | 0x193F | N |  |  | N |  |  | Y | 0x826A | 0x193F | N |  |  | N |  |  | Y | 0x826A | 0x193F
DC voltage alarm for DC cabinet N# N: 1–14 | 0x7BC1+(N-1)*138 | MA | 0x00: normal 0x01: overvoltage 0x02: undervoltage |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x1940 | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x1940 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x1940 | Y | 0x826A | 0x1940 | N |  |  | N |  |  | Y | 0x826A | 0x1940 | N |  |  | N |  |  | Y | 0x826A | 0x1940
Load fuse M for PDU 1 in DC cabinet N# N: 1–14; M: 1–42 | 0x7BC2+ (N-1)*138+ (M-1) | MA | 0x00: normal 0x01: alarm |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x1941~0x196A | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x1941~0x196A | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x1941~0x196A | Y | 0x826A | 0x1941~0x196A | N |  |  | N |  |  | Y | 0x826A | 0x1941~0x196A | N |  |  | N |  |  | Y | 0x826A | 0x1941~0x196A
Load fuse M for PDU 2 in DC cabinet N# N: 1–14; M: 1–42 | 0x7BC2+ (N-1)*138+ (M-1)+42 | MA | 0x00: normal 0x01: alarm |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x196B~0x1994 | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x196B~0x1994 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x196B~0x1994 | Y | 0x826A | 0x196B~0x1994 | N |  |  | N |  |  | Y | 0x826A | 0x196B~0x1994 | N |  |  | N |  |  | Y | 0x826A | 0x196B~0x1994
Load fuse M for PDU 3 in DC cabinet N# N: 1–14; M: 1–42 | 0x7BC2+ (N-1)*138+ (M-1)+42+42 | MA | 0x00: normal 0x01: alarm |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x1995~0x19BE | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x1995~0x19BE | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x1995~0x19BE | Y | 0x826A | 0x1995~0x19BE | N |  |  | N |  |  | Y | 0x826A | 0x1995~0x19BE | N |  |  | N |  |  | Y | 0x826A | 0x1995~0x19BE
Battery M Fuse Break for DC cabinet N# (N: 1–14; M: 1–10) | 0x7BC2+ (N-1)*138 + (M-1)+42+42+42 | MA | 0x00: normal 0x01: alarm |  | Y | N | N | N | N | Y | N | N |  | N |  | N |  | Y | N |  | Y | N | Y | N |  |  | N |  |  | Y | 0x826A | 0x19BF~0x19C8 | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x19BF~0x19C8 | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x826A | 0x19BF~0x19C8 | Y | 0x826A | 0x19BF~0x19C8 | N |  |  | N |  |  | Y | 0x826A | 0x19BF~0x19C8 | N |  |  | N |  |  | Y | 0x826A | 0x19BF~0x19C8
| (0x834C–0x834F) reserved | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| (0x8400–0x8430) Registers Reserved For ACB Group | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Charge Over Voltage | 0x8431+(N-1)*64 | WA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x35C0 | Y | 0x8019 | 0x35C0 | N |  |  | N |  |  | Y | 0x8019 | 0x35C0 | Y | 0x8019 | 0x35C0 | N |  |  | Y | 0x8019 | 0x35C0 | N |  |  | Y | 0x8019 | 0x35C0 | Y | 0x8019 | 0x35C0 | Y | 0x8019 | 0x35C0 | Y | 0x8019 | 0x35C0 | N |  |  | Y | 0x8019 | 0x35C0 | Y | 0x8019 | 0x35C0 | N |  |  | Y | 0x8019 | 0x35C0
Charge Over Current | 0x8432+(N-1)*64 | WA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x35C4 | Y | 0x8019 | 0x35C4 | N |  |  | N |  |  | Y | 0x8019 | 0x35C4 | Y | 0x8019 | 0x35C4 | N |  |  | N |  |  | N |  |  | Y | 0x8019 | 0x35C4 | Y | 0x8019 | 0x35C4 | Y | 0x8019 | 0x35C4 | Y | 0x8019 | 0x35C4 | N |  |  | Y | 0x8019 | 0x35C4 | Y | 0x8019 | 0x35C4 | N |  |  | Y | 0x8019 | 0x35C4
Overdischarge | 0x8433+(N-1)*64 | WA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x35C2 | Y | 0x8019 | 0x35C2 | N |  |  | N |  |  | Y | 0x8019 | 0x35C2 | Y | 0x8019 | 0x35C2 | N |  |  | Y | 0x8019 | 0x35C2 | N |  |  | Y | 0x8019 | 0x35C2 | Y | 0x8019 | 0x35C2 | Y | 0x8019 | 0x35C2 | Y | 0x8019 | 0x35C2 | N |  |  | Y | 0x8019 | 0x35C2 | Y | 0x8019 | 0x35C2 | N |  |  | Y | 0x8019 | 0x35C2
Heavy Load Warning | 0x8434+(N-1)*64 | WA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x35C6 | Y | 0x8019 | 0x35C6 | N |  |  | N |  |  | Y | 0x8019 | 0x35C6 | Y | 0x8019 | 0x35C6 | N |  |  | Y | 0x8019 | 0x35C6 | N |  |  | Y | 0x8019 | 0x35C6 | Y | 0x8019 | 0x35C6 | Y | 0x8019 | 0x35C6 | Y | 0x8019 | 0x35C6 | N |  |  | Y | 0x8019 | 0x35C6 | Y | 0x8019 | 0x35C6 | N |  |  | Y | 0x8019 | 0x35C6
Reversely Connection | 0x8435+(N-1)*64 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x35E3 | Y | 0x8019 | 0x35E3 | N |  |  | N |  |  | Y | 0x8019 | 0x35E3 | Y | 0x8019 | 0x35E3 | N |  |  | Y | 0x8019 | 0x35E3 | N |  |  | Y | 0x8019 | 0x35E3 | Y | 0x8019 | 0x35E3 | Y | 0x8019 | 0x35E3 | Y | 0x8019 | 0x35E3 | N |  |  | Y | 0x8019 | 0x35E3 | Y | 0x8019 | 0x35E3 | N |  |  | Y | 0x8019 | 0x35E3
Charge Over Temperature、Discharge Over Temperature | 0x8436+(N-1)*64 | MI | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x35BC/0x35BE | Y | 0x8019 | 0x35BC/0x35BE | N |  |  | N |  |  | Y | 0x8019 | 0x35BC/0x35BE | Y | 0x8019 | 0x35BC/0x35BE | N |  |  | Y | 0x8019 | 0x35BC/0x35BE | N |  |  | Y | 0x8019 | 0x35BC/0x35BE | Y | 0x8019 | 0x35BC/0x35BE | Y | 0x8019 | 0x35BC/0x35BE | Y | 0x8019 | 0x35BC/0x35BE | N |  |  | Y | 0x8019 | 0x35BC/0x35BE | Y | 0x8019 | 0x35BC/0x35BE | N |  |  | Y | 0x8019 | 0x35BC/0x35BE
Communication Failure | 0x8437+(N-1)*64 | MI | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x35B6 | Y | 0x8019 | 0x35B6 | N |  |  | N |  |  | Y | 0x8019 | 0x35B6 | Y | 0x8019 | 0x35B6 | N |  |  | Y | 0x8019 | 0x35B6 | N |  |  | Y | 0x8019 | 0x35B6 | Y | 0x8019 | 0x35B6 | Y | 0x8019 | 0x35B6 | Y | 0x8019 | 0x35B6 | N |  |  | Y | 0x8019 | 0x35B6 | Y | 0x8019 | 0x35B6 | N |  |  | Y | 0x8019 | 0x35B6
Low Temperature | 0x8438+(N-1)*64 | MI | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x35BA | Y | 0x8019 | 0x35BA | N |  |  | N |  |  | Y | 0x8019 | 0x35BA | Y | 0x8019 | 0x35BA | N |  |  | Y | 0x8019 | 0x35BA | N |  |  | Y | 0x8019 | 0x35BA | Y | 0x8019 | 0x35BA | Y | 0x8019 | 0x35BA | Y | 0x8019 | 0x35BA | N |  |  | Y | 0x8019 | 0x35BA | Y | 0x8019 | 0x35BA | N |  |  | Y | 0x8019 | 0x35BA
Discharge High Temperature Protection、Charge High Temperature Protection | 0x8439+(N-1)*64 | MI | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x35BD/0x35BF | Y | 0x8019 | 0x35BD/0x35BF | N |  |  | N |  |  | Y | 0x8019 | 0x35BD/0x35BF | Y | 0x8019 | 0x35BD/0x35BF | N |  |  | Y | 0x8019 | 0xF0C4 | N |  |  | Y | 0x8019 | 0x35BD/0x35BF | Y | 0x8019 | 0x35BD/0x35BF | Y | 0x8019 | 0x35BD/0x35BF | Y | 0x8019 | 0x35BD/0x35BF | N |  |  | Y | 0x8019 | 0x35BD/0x35BF | Y | 0x8019 | 0x35BD/0x35BF | N |  |  | Y | 0x8019 | 0x35BD/0x35BF
Low Temperature Protection | 0x843A+(N-1)*64 | MI | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x35BB/0x35E1/0x35E2 | Y | 0x8019 | 0x35BB/0x35E1/0x35E2 | N |  |  | N |  |  | Y | 0x8019 | 0x35BB/0x35E1/0x35E2 | Y | 0x8019 | 0x35BB/0x35E1/0x35E2 | N |  |  | Y | 0x8019 | 0x35E1/0x35E2 | N |  |  | Y | 0x8019 | 0x35BB/0x35E1/0x35E2 | Y | 0x8019 | 0x35BB/0x35E1/0x35E2 | Y | 0x8019 | 0x35BB/0x35E1/0x35E2 | Y | 0x8019 | 0x35BB/0x35E1/0x35E2 | N |  |  | Y | 0x8019 | 0x35BB/0x35E1/0x35E2 | Y | 0x8019 | 0x35BB/0x35E1/0x35E2 | N |  |  | Y | 0x8019 | 0x35BB/0x35E1/0x35E2
Overcharge Protection | 0x843B+(N-1)*64 | MI | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x35C1 | Y | 0x8019 | 0x35C1 | N |  |  | N |  |  | Y | 0x8019 | 0x35C1 | Y | 0x8019 | 0x35C1 | N |  |  | Y | 0x8019 | 0x35C1 | N |  |  | Y | 0x8019 | 0x35C1 | Y | 0x8019 | 0x35C1 | Y | 0x8019 | 0x35C1 | Y | 0x8019 | 0x35C1 | N |  |  | Y | 0x8019 | 0x35C1 | Y | 0x8019 | 0x35C1 | N |  |  | Y | 0x8019 | 0x35C1
Overdischarge Protection | 0x843C+(N-1)*64 | MI | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x35C3 | Y | 0x8019 | 0x35C3 | N |  |  | N |  |  | Y | 0x8019 | 0x35C3 | Y | 0x8019 | 0x35C3 | N |  |  | Y | 0x8019 | 0x35C3 | N |  |  | Y | 0x8019 | 0x35C3 | Y | 0x8019 | 0x35C3 | Y | 0x8019 | 0x35C3 | Y | 0x8019 | 0x35C3 | N |  |  | Y | 0x8019 | 0x35C3 | Y | 0x8019 | 0x35C3 | N |  |  | Y | 0x8019 | 0x35C3
Charge Overcurrent Protection、Discharge Overcurrent Protection | 0x843D+(N-1)*64 | MI | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | Y | N |  | Y | N | Y | N |  |  | Y | 0x8019 | 0x35C5/0x35C7 | Y | 0x8019 | 0x35C5/0x35C7 | N |  |  | N |  |  | Y | 0x8019 | 0x35C5/0x35C7 | Y | 0x8019 | 0x35C5/0x35C7 | N |  |  | Y | 0x8019 | 0x35C7 | N |  |  | Y | 0x8019 | 0x35C5/0x35C7 | Y | 0x8019 | 0x35C5/0x35C7 | Y | 0x8019 | 0x35C5/0x35C7 | Y | 0x8019 | 0x35C5/0x35C7 | N |  |  | Y | 0x8019 | 0x35C5/0x35C7 | Y | 0x8019 | 0x35C5/0x35C7 | N |  |  | Y | 0x8019 | 0x35C5/0x35C7
Battery Alarm For ACB | 0x843E+(N-1)*64 |  | 0: normal 1: alarm bit0: Abnormal Shutdown, Severity: MA bit1: SOH Subhealth, Severity: MI bit2: SOH Low, Severity: MA bit3~bit15: Reserved |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| (0x843F~0x8470+(N-1)*64) Registers Reserved For ACB | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| (0x8C31–0x8FFF) Registers Reserved For ACB | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Communication Failure N:1-4 | 0xE000+(N-1)*16 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Abnormal Input Voltage N:1-4 | 0xE001+(N-1)*16 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Over Temperature N:1-4 | 0xE002+(N-1)*16 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Abnormal Input Freqency N:1-4 | 0xE003+(N-1)*16 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Abnormal Shutdown N:1-4 | 0xE004+(N-1)*16 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Phase Sequence Error N:1-4 | 0xE005+(N-1)*16 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Not Fully Plugged N:1-4 | 0xE006+(N-1)*16 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Module Fault N:1-4 | 0xE007+(N-1)*16 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Module Protected N:1-4 | 0xE008+(N-1)*16 | MI | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Address Conflict N:1-4 | 0xE009+(N-1)*16 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Bypass Input Failure N:1-4 | 0xE00A+(N-1)*16 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| Reserved (0xE00B–0xE00F) | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Output Phase Failure N:1-4 | 0xE040+(N-1)*8 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Internal CAN Fault N:1-4 | 0xE041+(N-1)*8 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Inter-shelf CAN Fault N:1-4 | 0xE042+(N-1)*8 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Inverter Missing N:1-4 | 0xE043+(N-1)*8 | MI | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Wrong Inverter Slot N:1-4 | 0xE044+(N-1)*86 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit Bypass Module Missing N:1-4 | 0xE045+(N-1)*8 | MI | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Unit All Inverters Communication Failure N:1-4 | 0xE046+(N-1)*8 | MI | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| Reserved (0xE047–0xE047) | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Group All modules Fail to Communicate | 0xE060 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Group module Missing | 0xE061 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Group Address Conflict | 0xE062 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| Reserved(0xE063~0xE06F) | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Communication Failure N:1-32 | 0xE070+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load1 Fuse Broken N:1-32 | 0xE071+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load2 Fuse Broken N:1-32 | 0xE072+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load3 Fuse Broken N:1-32 | 0xE073+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load4 Fuse Broken N:1-32 | 0xE074+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Total Load Overcurrent N:1-32 | 0xE075+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load1 Overcurrent Protection N:1-32 | 0xE076+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load2 Overcurrent Protection N:1-32 | 0xE077+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load3 Overcurrent Protection N:1-32 | 0xE078+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load4 Overcurrent Protection N:1-32 | 0xE079+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load1 Disconnected N:1-32 | 0xE07A+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load2 Disconnected N:1-32 | 0xE07B+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load3 Disconnected N:1-32 | 0xE07C+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load4 Disconnected N:1-32 | 0xE07D+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Board Fault N:1-32 | 0xE07E+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Board High Temperature N:1-32 | 0xE07F+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Board High Temperature Protection N:1-32 | 0xE080+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load1 Control Fault N:1-32 | 0xE081+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load2 Control Fault N:1-32 | 0xE082+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load3 Control Fault N:1-32 | 0xE083+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load4 Control Fault N:1-32 | 0xE084+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Module Not Activated N:1-32 | 0xE085+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
iDCDU Load Fuse Broken N:1-32 | 0xE086+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| Reserved (0xE087~0xE08F) | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
ECM Communication Failure N:1-8 | 0xE470+(N-1)*16 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
ECM SPD Trip N:1-8 | 0xE471+(N-1)*16 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
ECM Address Conflict N:1-8 | 0xE472+(N-1)*16 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
ECM Freq Sync Failure N:1-8 | 0xE473+(N-1)*16 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
ECM Carrier Sync Failure N:1-8 | 0xE474+(N-1)*16 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
ECM Bypass Signal Failure N:1-8 | 0xE475+(N-1)*16 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
ECM Turn off Abnormally N:1-8 | 0xE476+(N-1)*16 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
ECM E2PROM Fault N:1-8 | 0xE477+(N-1)*16 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
ECM Bypass Over Load N:1-8 | 0xE478+(N-1)*16 | MI | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| Reserved (0xE479~0xE47F) | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| Registers(0xE570~) | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Module Communication Failure N:1-4 | 0xE570+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Discharge High Temperature Protection N:1-4 | 0xE571+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Charge High Temperature Protection N:1-4 | 0xE572+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Charge Low Temperature Protection N:1-4 | 0xE573+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Discharge Low Temperature Protection N:1-4 | 0xE574+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Charge Over Voltage Protected N:1-4 | 0xE575+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Disharge Under Voltage Protected N:1-4 | 0xE576+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Module Over Temperature Protection N:1-4 | 0xE577+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Overload Protection N:1-4 | 0xE578+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Battery Cell 1 Fault N:1-4 | 0xE579+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Battery Cell 2 Fault N:1-4 | 0xE57A+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM PV Input Over Voltage Protected N:1-4 | 0xE57B+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM PV Input Under Voltage Protected N:1-4 | 0xE57C+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM 12V Output Overload Protected N:1-4 | 0xE57D+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Bus Bar Under Voltage Protected N:1-4 | 0xE57E+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM External Cause 12V Over Voltage Protection N:1-4 | 0xE57F+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
SSM Module Fail N:1-4 | 0xE580+(N-1)*32 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | N | Y | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| Reserved (0xE581~0xE58F+(N-1)*32) | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| Registers(0xE5F0~) | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Fault N:1-32 | 0xE5F0+(N-1)*8 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Inverter Protection N:1-32 | 0xE5F1+(N-1)*8 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Communication Failure N:1-32 | 0xE5F2+(N-1)*8 | MA | 0x00: normal 0x01: alarm |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  | Y | N | Y | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
| Reserved (0xE5F3~0xE5F7+(N-1)*8) | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
DC Output Distribution Load-iCBD N Alarm N:1-62 | 0xE6F0+(N-1) |  | 0: normal 1: alarm bit0: Load Overcurrent Protection, Severity: MA bit1: Load Fuse Broken, Severity: MA bit2: Breaker Abnormal, Severity: MA bit3: Disconnected, Severity: MA bit4: Disconnect Warning, Severity: MA bit5: Breaker Not Detected, Severity: MA bit6: Heavy Load Warning, Severity: MI bit7~bit15: Reserved |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Reserved (0xE72E~0xE72F)
24V Module Group Alarm | 0xE730 |  | 0: normal 1: alarm bit0: All 24V Module Fail to Communicate , Severity: MA bit1: Module Missing, Severity: MA |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
24V Module Alarm N:1-8 | 0xE731+(N-1) |  | 0: normal 1: alarm bit0: Module Communication Failure, Severity: MI bit1: Module Protection, Severity: MI bit2: Module Fault , Severity: MA bit3~bit15: Reserved |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Reserved (0xE739~~0xE73F)
iDMU M Load-iCBD N Alarm M:1~4 N:1-34 | 0xE740+(M-1)*34+(N-1) |  | 0: normal 1: alarm bit0: Load Overcurrent Protection, Severity: MA bit1: Load Fuse Broken, Severity: MA bit2: Breaker Abnormal, Severity: MA bit3: Disconnected, Severity: MA bit4: Disconnect Warning, Severity: MA bit5: Breaker Not Detected, Severity: MA bit6: Heavy Load Warning, Severity: MI bit7~bit15: Reserved |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Reserved (0xE7C8~~0xE7CF)
PV Adapter1–N (N=18) Alarm | 0xE7D0+(N-1) |  | 0: normal 1: alarm bit0: Hardware Fault, Severity: MA bit1: Output Short circuit, Severity: MA bit2: Input Vervoltage, Severity: MA bit3: Communication Failure, Severity: MI bit4: Module Overtemperature, Severity: MA bit5~bit15: Reserved |  | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | Y | 0x81D5 | bit0： 0x59AB：硬件故障； bit1： 0x59AA：输出短路； bit2： 0x59A8：输入过压； bit:3： 0x59A7：通信失败； bit4： 0x59A9：模块高温； | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N
Note: MI-minor alarm MA-major alarm CA-critical alarm WA-warning
| Registers(0xE7E1~) | [22 empty] | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N |  |  | N